{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["al_info"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"al_info","index":0,"n_rows":483,"n_cols":23,"rows_kept":483,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["DOMAIN","Groep","SEQ_NBR","Nummer","Tag naam","Cond","Limiet","Deadband","Alarm tekst","VAR1","VAR2","VAR3","VAR4","Prioriteit","Area","TIME","TIMEFMT","GMASK","MASK","Status tag","NOTIFY","SUBJECT","ROWID"]
["SHARED","ALARM","0000010000","220","NOODUIT","ON","0",null,"Noodstop brander bediend",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B48-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000020000","270","KETEL_AVW","ON","0",null,"Aanvullende ketelvoorwaarden niet voldaan",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B4D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000030000","310","TS_169","ON","0",null,"Temperatuur bed 1  >  1000 grd. C",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B51-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000040000","320","TS_170","ON","0",null,"Temperatuur bed 2  >  1000 grd. C",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B52-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000050000","330","DPS_160","ON","0",null,"Bedhoogte  <  minimaal",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B53-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000060000","340","WATCHDOG","ON","0",null,"Watchdog storing",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B54-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000070000","350","PAH_163","ON","0",null,"Vuurhaarddruk  >  + 0.1 mbar",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B55-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000080000","360","PS_180","ON","0",null,"Stuurlucht druk  <  4 bar",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B56-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000090000","370","PS_174","ON","0",null,"Aansteek luchtdruk  <  30 mbar",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B57-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000100000","380","PS_171_1","ON","0",null,"Gasdruk  <  2 bar",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B58-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000110000","390","PS_171_2","ON","0",null,"Gasdruk  >  3 bar",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B59-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000120000","400","XZS_168_169","ON","0",null,"Hoofdgasventielen niet gesloten",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B5A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000130000","410","FS_198_199","ON","0",null,"Verbrandingsluchtflow  <  minimaal",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B5B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000140000","420","TZS_183","ON","0",null,"Gasregelklep bed1 niet in startpos",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B5C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000150000","430","TZS_184","ON","0",null,"Gasregelklep bed2 niet in startpos",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B5D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000160000","440","FS_198199","ON","0",null,"Verbrandingsluchtflow  <  90 procent",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B5E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000170000","450","VLAM_ST","ON","0",null,"Vlamstoring hoofdbranders",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B5F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000180000","460","PDS_158","ON","0",null,"Verbrandingsluchtdruk  <  minimaal",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B60-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000190000","470","XS_173","ON","0",null,"Gaslek in hoofdventielen",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B61-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000200000","480","BR_152","OFF","0",null,"Aansteekbrander 1 in alarm",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B62-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000210000","490","BR_153","OFF","0",null,"Aansteekbrander 2 in alarm",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{7C610B63-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000220000","850","KLEPPEN_AL[16]","ON","0",null,"Klep XEV-815 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{08B66EBA-265F-11D9-9709-00087440B138}"]
["SHARED","ALARM","0000230000","860","KLEPPEN_AL[17]","ON","0",null,"Snelsluit klep PV-1008 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{7C610B66-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000240000","870","KLEPPEN_AL[21]","ON","0",null,"Klep XEV-818 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{08B66EB5-265F-11D9-9709-00087440B138}"]
["SHARED","ALARM","0000250000","880","KLEPPEN_AL[22]","ON","0",null,"Klep XEV-800 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{08B66EB3-265F-11D9-9709-00087440B138}"]
["SHARED","ALARM","0000260000","890","KLEPPEN_AL[24]","ON","0",null,"Klep XEV-162.1 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{24B35B81-2673-11D9-9709-00087440B138}"]
["SHARED","ALARM","0000270000","900","KLEPPEN_AL[25]","ON","0",null,"Klep XEV-162.2 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{24B35B7F-2673-11D9-9709-00087440B138}"]
["SHARED","ALARM","0000280000","910","KLEPPEN_AL[26]","ON","0",null,"Klep XEV-162.3 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{24B35B7D-2673-11D9-9709-00087440B138}"]
["SHARED","ALARM","0000290000","1010","MOTOR_AL[10]","ON","0",null,"Roerwerk M-802 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B69-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000300000","1020","MOTOR_AL[11]","ON","0",null,"Roerwerk M-804 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B6A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000310000","1030","MOTOR_AL[12]","ON","0",null,"Pomp P-800 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B6B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000320000","1040","MOTOR_AL[16]","ON","0",null,"Pomp P-802A in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B6C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000330000","1090","MOTOR_AL[42]","ON","0",null,"Schroef A-150 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B71-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000340000","1100","MOTOR_AL[43]","ON","0",null,"Schroef A-151 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B72-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000350000","1110","MOTOR_AL[44]","ON","0",null,"Schroef A-161 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B73-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000360000","1120","MOTOR_AL[45]","ON","0",null,"Schroef A-162 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B74-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000370000","1130","MOTOR_AL[47]","ON","0",null,"Schroef A-150.1 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B75-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000380000","1140","MOTOR_AL[48]","ON","0",null,"Schroef A-152 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B76-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000390000","1150","MOTOR_AL[49]","ON","0",null,"Sluis A-160.3 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B77-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000400000","1160","MOTOR_AL[50]","ON","0",null,"Sluis A-160.1 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B78-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000410000","1170","MOTOR_AL[52]","ON","0",null,"Sluis A-179 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B79-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000420000","1180","MOTOR_AL[53]","ON","0",null,"Sluis A-160.2 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B7A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000430000","1190","MOTOR_AL[54]","ON","0",null,"Pomp P-805 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B7B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000440000","1200","MOTOR_AL[55]","ON","0",null,"Shredder A-153 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B7C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000450000","1210","MOTOR_AL[56]","ON","0",null,"Blower K-150 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B7D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000460000","1220","MOTOR_AL[57]","ON","0",null,"Blower K-151.1 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B7E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000470000","1230","MOTOR_AL[58]","ON","0",null,"Blower K-152 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B7F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000480000","1240","MOTOR_AL[59]","ON","0",null,"Pomp P-804 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B80-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000490000","1250","MOTOR_AL[60]","ON","0",null,"Schroef A-152.1 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B81-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000500000","1260","MOTOR_AL[62]","ON","0",null,"Pomp P-815 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B82-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000510000","1270","MOTOR_AL[63]","ON","0",null,"Blower K-158 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B83-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000520000","1280","MOTOR_AL[64]","ON","0",null,"Blower K-151.2 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B84-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000530000","1290","MOTOR_AL[65]","ON","0",null,"Pomp P-815.2 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B85-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000540000","1300","MOTOR_AL[66]","ON","0",null,"Blower K-818.2 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B86-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000550000","1310","MOTOR_AL[70]","ON","0",null,"Pomp P-816A in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B87-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000560000","1320","MOTOR_AL[71]","ON","0",null,"Pomp P-816B in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B88-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000570000","1330","MOTOR_AL[72]","ON","0",null,"Blower K-172 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B89-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000580000","1340","MOTOR_AL[73]","ON","0",null,"Blower K-175 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B8A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000590000","1350","MOTOR_AL[75]","ON","0",null,"Pomp P-950 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B8B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000600000","1360","MOTOR_AL[77]","ON","0",null,"Blower K-820B in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B8C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000610000","1370","MOTOR_AL[78]","ON","0",null,"Pomp P-910A in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B8D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000620000","1380","MOTOR_AL[79]","ON","0",null,"Pomp P-910S in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B8E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000630000","1390","MOTOR_AL[81]","ON","0",null,"Snelsluitklep XEV-157 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B8F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000640000","1400","MOTOR_AL[82]","ON","0",null,"Wasmachine in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B90-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000650000","1410","MOTOR_AL[83]","ON","0",null,"Blower K-818.1 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B91-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000660000","1420","MOTOR_AL[84]","ON","0",null,"Pomp P-819 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B92-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000670000","1430","MOTOR_AL[86]","ON","0",null,"Blower K-820A in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B93-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000680000","1460","MOTOR_AL[89]","ON","0",null,"Schroef A-151.1 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{7C610B96-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000690000","2390","LI_800_1",">=","0",null,"Niveau indicatie opslag-tank V-800-A",null,null,"DATETIME","SECTIME","9","RT-TREND_TAGS",null,null,"NO",{"$nulls":4},"{7C610B97-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000700000","2500","FISAL_158","ON","0",null,"Verbrandingslucht bed 2 laag",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610B9C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000710000","2510","FISALL_158","ON","0",null,"Verbrandingslucht bed 2 zeer laag",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610B9D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000720000","2520","FISAL_159","ON","0",null,"Verbrandingslucht bed 1 laag",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610B9E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000730000","2530","FISALL_159","ON","0",null,"Verbrandingslucht bed 1 zeer laag",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610B9F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000740000","2550","FAH_171","ON","0",null,"Aardgasflow naar bed 1 hoog",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BA1-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000750000","2560","FAL_171","ON","0",null,"Aardgasflow naar bed 1 laag",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BA2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000760000","2570","FAH_172","ON","0",null,"Aardgasflow naar bed 2 hoog",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BA3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000770000","2580","FAL_172","ON","0",null,"Aardgasflow naar bed 2 laag",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BA4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000780000","2590","FSAL_815_1","ON","0",null,"Lage flow naar scrubber C-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BA5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000790000","2600","FSAL_815_2","ON","0",null,"Lage flow naar quench C-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BA6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000800000","2670","FAL_911","OFF","0",null,"Lage flow koelwater E-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[19]",null,null,"{7C610BAD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000810000","2690","FAL_913","OFF","0",null,"Lage flow koelwater nieuw->oud systeem",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[44]",null,null,"{7C610BAF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000820000","2700","FSAL_951","OFF","0",null,"Lage flow sealwater",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BB0-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000830000","2830","LSAH_118","OFF","0",null,"Hoog niveau vat B-163",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[30]",null,null,"{7C610BBD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000840000","2900","LALL_152","ON","0",null,"Zeer laag niveau nevendrum V-150",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BC4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000850000","2980","LS_921","ON","0",null,"Niveau alarm doekenfilter 2, F-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[27]",null,null,"{7C610BCC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000860000","2990","LA_921","OFF","0",null,"Niveau meting doekenfilter 2 F-150 defect",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BCD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000870000","3000","LS_922","ON","0",null,"Niveau alarm doekenfilter 3, F-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[28]",null,null,"{7C610BCE-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000880000","3010","LA_922","OFF","0",null,"Niveau meting doekenfilter 3 F-150 defect",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BCF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000890000","3020","LSAH_167","ON","0",null,"Hoog niveau bunker B-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BD0-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000900000","3030","LSAL_167","ON","0",null,"Laag niveau bunker B-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BD1-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000910000","3040","LSAH_168","ON","0",null,"Hoog niveau bunker B-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BD2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000920000","3050","LSAL_168","ON","0",null,"Laag niveau bunker B-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BD3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000930000","3060","LSALL_800_2","OFF","0",null,"Zeer laag niveau in opslagtank V-800A",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[33]",null,null,"{7C610BD4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000940000","3070","LSAHH_800_3","OFF","0",null,"Zeer hoog niveau in opslagtank V-800A",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[34]",null,null,"{7C610BD5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000950000","3080","LAH_800_4","ON","0",null,"Hoog niveau produkt tank V-800B",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BD6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000960000","3090","LAHH_800_4","ON","0",null,"Zeer hoog niveau produkt tank V-800B",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BD7-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000970000","3100","LSALL_800_5","OFF","0",null,"Zeer laag niveau in opslagtank V-800B",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[35]",null,null,"{7C610BD8-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000980000","3110","LSAHH_800_7","OFF","0",null,"Hoog niveau in tankwagen",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[18]",null,null,"{7C610BD9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0000990000","3120","LSALL_802_2","OFF","0",null,"Zeer laag niveau in hydroxide tank V-802",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[40]",null,null,"{7C610BDA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001000000","3130","LAHH_800_1","ON","0",null,"Zeer hoog niveau produkt tank V-800A",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BDB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001010000","3140","LAH_800_1","ON","0",null,"Hoog niveau produkt tank V-800A",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BDC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001020000","3150","LAL_800_1","ON","0",null,"Laag niveau produkt tank V-800A",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BDD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001030000","3160","LALL_800_1","ON","0",null,"Zeer laag niveau produkt tank V-800A",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BDE-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001040000","3170","LAHH_802_1","ON","0",null,"Zeer hoog niveau in hydroxide tank V-802",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BDF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001050000","3180","LAH_802_1","ON","0",null,"Hoog niveau in hydroxide tank V-802",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE0-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001060000","3190","LAL_802_1","ON","0",null,"Laag niveau in hydroxide tank V-802",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE1-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001070000","3200","LAH_804_1","ON","0",null,"Hoog niveau in eind-ox tank V-804",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001080000","3210","LAL_804_1","ON","0",null,"Laag niveau in eind-ox tank V-804",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001090000","3220","LSALL_804_2","OFF","0",null,"Zeer laag niveau in final ox. tank V-804",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[36]",null,null,"{7C610BE4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001100000","3230","LSAHH_804_3","OFF","0",null,"Zeer hoog niveau in final ox. tank V-804",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[37]",null,null,"{7C610BE5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001110000","3240","LAL_815_1","ON","0",null,"Laag niveau (<35) in scrubber C-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001120000","3250","LAH_815_1","ON","0",null,"Hoog niveau (>70) in scrubber C-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE7-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001130000","3260","LALL_815_2","OFF","0",null,"Zeer laag niveau in scrubber C-815",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[38]",null,null,"{7C610BE8-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001140000","3270","LAH_816","OFF","0",null,"Hoog niveau waskolom C-816",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BE9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001150000","3280","LAH_817","OFF","0",null,"Hoog niveau waskolom C-817",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BEA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001160000","3290","LAH_818","OFF","0",null,"Hoog niveau in waskolom C-818",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BEB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001170000","3300","LAHH_820_1","ON","0",null,"Zeer hoog niveau pompvat V-820 uit",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BEC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001180000","3310","LAH_820_1","ON","0",null,"Hoog niveau pompvat V-820 uit",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BED-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001190000","3320","LAL_820_1","ON","0",null,"Laag niveau pompvat V-820 uit",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BEE-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001200000","3330","LSALL_820_2","OFF","0",null,"Zeer laag niveau pompvat V-820 uit",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[41]",null,null,"{7C610BEF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001210000","3340","LSALL_820_3","OFF","0",null,"Zeer laag niveau pompsump V-820",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[42]",null,null,"{7C610BF0-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001220000","3360","LSAL_910","OFF","0",null,"Laag niveau in koelwater tank V-910",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[21]",null,null,"{7C610BF2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001230000","3370","LSALL_910","OFF","0",null,"Zeer laag niveau in koelwater tank V-910",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[22]",null,null,"{7C610BF3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001240000","3380","LAL_913","ON","0",null,"Laag niveau in sealwatertank V-950",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BF4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001250000","3430","TS_155_1","ON","0",null,"Buitentemperatuur  <  +1 grd.C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BF9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001260000","3440","TS_155_2","ON","0",null,"Buitentemperatuur  <  -5 grd.C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BFA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001270000","3450","TAH_186","ON","0",null,"Hoge temperatuur in katbunker B-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BFB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001280000","3470","TAH_187","ON","0",null,"Hoge temperatuur in katbunker B-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610BFD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001290000","3530","TAH_192","ON","0",null,"Hoge temperatuur in katbunker B-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C03-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001300000","3540","TAHH_192","ON","0",null,"Zeer hoge temperatuur in katbunker B-150",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C04-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001310000","3550","TAH_193","ON","0",null,"Hoge temperatuur in katbunker B-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C05-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001320000","3560","TAHH_193","ON","0",null,"Zeer hoge temperatuur in katbunker B-150",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C06-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001330000","3570","TAH_194","ON","0",null,"Hoge temperatuur in katbunker B-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C07-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001340000","3580","TAHH_194","ON","0",null,"Zeer hoge temperatuur in katbunker B-151",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C08-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001350000","3590","TAH_195","ON","0",null,"Hoge temperatuur in katbunker B-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C09-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001360000","3600","TAHH_195","ON","0",null,"Zeer hoge temperatuur in katbunker B-151",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C0A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001370000","3610","TSAH_813","ON","0",null,"Temperatuur in uitlaat van C-815 > 70 grd.C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C0B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001380000","3620","TSAHH_813","ON","0",null,"Temperatuur in uitlaat van C-815 > 80 grd.C",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C0C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001390000","3630","TSAHH_813","ON","0",null,"MK-818 stop door hoge temp. uitlaat C-815",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C0D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001400000","3640","dPAH_814_1","OFF","0",null,"Hoge verschildruk in demister van C-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[47]",null,null,"{7C610C0E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001410000","3650","dPAH_814_2","ON","0",null,"Hoge verschildruk in warmtewisselaar E-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C0F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001420000","3660","PAH_812","ON","0",null,"Hoge druk in rookgas naar quench Z-815",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C10-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001430000","3670","PAHH_812","ON","0",null,"Zeer hoge druk in rookgas naar quench Z-815",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C11-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001440000","3680","TSAHH_814_1","OFF","0",null,"Zeer hoge temp. in uitlaat v. koeler v. Z815",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C12-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001450000","3690","TAH_157","ON","0",null,"Hoge temperatuur na A-192",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C13-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001460000","3700","QA_151","ON","0",null,"Percentage stof in rookgas hoog",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C14-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001470000","3710","QAHH_151","ON","0",null,"Percentage stof in rookgas te hoog",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C15-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001480000","3720","dPAH_166","ON","0",null,"Hoge verschildruk over doekenfilter F-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C16-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001490000","3730","dPAHH_166","ON","0",null,"Zeer hoge verschildruk over doekenfilter",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C17-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001500000","3740","QAHH_811_1","ON","0",null,"Zeer hoog gehalte SO2 in rookgas",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C18-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001510000","3750","QAH_811_1","ON","0",null,"Hoog gehalte SO2 in rookgas",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C19-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001520000","3760","QAHH_820_2","ON","0",null,"Zeer hoge dichtheid in V-820",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C1A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001530000","3770","QAH_820_2","ON","0",null,"Hoge dichtheid in V-820",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C1B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001540000","3780","QAL_820_2","ON","0",null,"Lage dichtheid in V-820",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C1C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001550000","3790","QALL_820_2","ON","0",null,"Zeer lage dichtheid in V-820",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C1D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001560000","3800","TAL_171","ON","0",null,"Lage temp. in rookgas naar sproeikoeler C150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C1E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001570000","3810","TAH_171","ON","0",null,"Hoge temp. in rookgas naar sproeikoeler C150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C1F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001580000","3820","TAH_172","ON","0",null,"Hoge temp. in rookgas van sproeikoeler C150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C20-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001590000","3830","TAH_804","ON","0",null,"Hoge temperatuur V-804",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C21-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001600000","3840","TAHH_804","ON","0",null,"Zeer hoge temperatuur V-804",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C22-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001610000","3850","dPALL_160","ON","0",null,"Bedhoogte  <  10 cm",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C23-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001620000","3860","dPAL_160","ON","0",null,"Bedhoogte  <  15 cm",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C24-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001630000","3870","dPAH_160_2","ON","0",null,"Bedhoogte  >  145 cm",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C25-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001640000","3880","dPAHH_160_1","ON","0",null,"Bedhoogte  >  150 cm",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C26-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001650000","3890","TAH_160_2","ON","0",null,"Temperatuur bed 1 > 900 grd.C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C27-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001660000","3900","TAHH_160_2","ON","0",null,"Temperatuur bed 1 > 950 grd.C",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C28-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001670000","3910","TAH_161_2","ON","0",null,"Temperatuur bed 2 > 900 grd.C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C29-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001680000","3920","TAHH_161_2","ON","0",null,"Temperatuur bed 2 > 950 grd.C",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C2A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001690000","3930","dPS_169","OFF","0",null,"Verschildruk doekenfilter > 18 mbar",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C2B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001700000","3950","PSAH_820_1","OFF","0",null,"Hoge persdruk ventilator K-820-A",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C2D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001710000","3960","PSAH_820_3","OFF","0",null,"Hoge persdruk ventilator K-820-B",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C2E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001720000","3970","dPAH_818_8","OFF","0",null,"Hoge verschildruk over sproeiplaat C-818",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C2F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001730000","3980","TAL_189","ON","0",null,"Temperatuur warme hal < 5 grd. C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C30-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001740000","3990","LAL_171_1","OFF","0",null,"SEAC - Laag niveau vat V-156",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[29]",null,null,"{7C610C31-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001750000","4000","LAH_171_1","OFF","0",null,"SEAC - Hoog niveau vat V-156",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[32]",null,null,"{7C610C32-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001760000","4010","LALL_171_2","OFF","0",null,"SEAC - Zeer laag niveau vat V-156",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[31]",null,null,"{7C610C33-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001770000","4020","XA_152","ON","0",null,"SEAC - Leveltransmitter defect",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C34-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001780000","4030","PAL_156","OFF","0",null,"SEAC - Lage druk perszijde P-156.1 / P-156.2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C35-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001790000","4040","TAH_156_1","ON","0",null,"SEAC - Hoge temperatuur water naar P-156.1/2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C36-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001800000","4050","XA_153","ON","0",null,"SEAC - Pomp P-156.2 loopt, geen stroming",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C37-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001810000","4060","XA_154","ON","0",null,"SEAC - Pomp P-156.1 loopt, geen stroming",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C38-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001820000","4070","TA_157_1","ON","0",null,"SEAC - Overload error P-156.2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C39-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001830000","4080","TA_157_2","ON","0",null,"SEAC - Overload error P-156.1",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C3A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001840000","4090","ZA_150","OFF","0",null,"SEAC - Error mode control system",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C3B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001850000","4100","PAL_129","OFF","0",null,"SEAC - Lage inlaatdruk klepstation water",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C3C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001860000","4110","PAL_115","OFF","0",null,"SEAC - Lage inlaatdruk klepstation lucht",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C3D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001870000","4120","PAH_118","OFF","0",null,"SEAC - Lage uitlaatdruk klepstation lucht",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C3E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001880000","4130","FSAL_811_1","OFF","0",null,"Lage flow in SO2 analyser",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C3F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001890000","4140","PSAH_167_1","OFF","0",null,"Werkluchtdruk  >  6 bar",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C40-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001900000","4150","PSAH_167_2","OFF","0",null,"Werkluchtdruk  >  3.5 bar",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C41-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001910000","4160","TAHH_165_2","ON","0",null,"Zeer hoge temperatuur in freeboard",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C42-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001920000","4170","XZA_105","OFF","0",null,"Explosieluik van oven geopend",null,null,"DATETIME","SECTIME","7","TABLE1",null,null,"NO",null,"ALARM_STAT[6]",null,null,"{7C610C43-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001930000","4180","XA_901","OFF","0",null,"Voormelding Bucholz relais",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C44-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001940000","4220","PALL_919","ON","0",null,"Zeer lage druk perslucht systeem",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C48-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001950000","4230","PAL_919","ON","0",null,"Lage druk perslucht systeem",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C49-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001960000","4370","TI_163_1",">","950",null,"Temperatuur free-board > 950 grd.C",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C57-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001970000","4380","VIBRO818_H","OFF","0",null,"Voor alarm Vibrocontrol ventilator K818.1",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[53]",null,null,"{7C610C58-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001980000","4390","VIBRO818_HH","OFF","0",null,"Hoog alarm Vibrocontrol ventilator K-818.1",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[43]",null,null,"{7C610C59-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0001990000","4400","VIBRO_H","OFF","0",null,"Voor alarm Vibrocontrol MK-151.1",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[45]",null,null,"{7C610C5A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0002000000","4410","VIBRO_HH","OFF","0",null,"Hoog alarm Vibrocontrol MK-151.1",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[50]",null,null,"{7C610C5B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0002010000","4420","LS_920","ON","0",null,"Niveau alarm doekenfilter 1, F150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C5C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0002020000","4430","NOODVD_STATUS","OFF","0",null,"Noodvoeding RTO in storing",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C5D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0002030000","4440","NOODVD_NET","OFF","0",null,"Netvoeding noodvoeding RTO niet aanwezig",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{7C610C5E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","ALARM","0002040000","4490","TI_149_4",">","100","5","Hoge temperatuur perslucht voorverwarmer",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA3BD-5452-11D9-970A-00087440B138}"]
["SHARED","ALARM","0002050000","4500","VIBRO818_2_H","OFF","0",null,"Voor alarm Vibrocontrol ventilator K818.2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[54]",null,null,"{F8FBA49F-ABF5-11D9-9718-00087440B138}"]
["SHARED","ALARM","0002060000","4510","VIBRO818_2_HH","OFF","0",null,"Hoog alarm Vibrocontrol ventilator K-818.2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[46]",null,null,"{F8FBA4A1-ABF5-11D9-9718-00087440B138}"]
["SHARED","ALARM","0002070000","4520","VIBRO151_2_H","OFF","0",null,"Voor alarm Vibrocontrol MK-151.2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[51]",null,null,"{73C14FD5-E3F1-11D9-971D-00087440B138}"]
["SHARED","ALARM","0002080000","4530","VIBRO151_2_HH","OFF","0",null,"Hoog alarm Vibrocontrol MK-151.2",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[52]",null,null,"{73C14FD7-E3F1-11D9-971D-00087440B138}"]
["SHARED","MELD","0000010000","10","SPANNING","ON","0",null,"Spanning ketelbesturing aanwezig",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C84-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000020000","20","TE_162_2","ON","0",null,"Spoeltijd overbrugging in",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C85-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000030000","30","VWCIRCUIT","ON","0",null,"Voorwaarden circuit gesloten",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C86-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000040000","40","REGELVRIJ","ON","0",null,"Regelvrijgave TIC automatisch",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C87-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000050000","50","REGEL_VRIJ","ON","0",null,"Regelvrijgave branderbesturing",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C88-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000060000","60","TESTDRUK","ON","0",null,"Test verbr.lucht drukschakelaar",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C89-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000070000","70","PROGSTART","ON","0",null,"Programma startbereid",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C8A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000080000","80","REGSPOEL","ON","0",null,"Regeling naar spoelstand",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C8B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000090000","90","REGSPOEL_90","ON","0",null,"Spoelluchtflow > 90 procent",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C8C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000100000","100","SPOELTIJD","ON","0",null,"Spoeltijd loopt",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C8D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000110000","110","TS_158159","ON","0",null,"Spoeltijd overbrugging in (> 600)",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C8E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000120000","120","REGSTART","ON","0",null,"Regeling naar startstand",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C8F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000130000","130","PROGLOOP","ON","0",null,"Programma loopt",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C90-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000140000","140","AAN_CONT","ON","0",null,"Aansteekbranders continue",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C91-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000150000","150","ONTSTEK","ON","0",null,"Ontsteking in",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C92-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000160000","160","XEV_168","ON","0",null,"Hoofdventiel XEV-168 open",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C93-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000170000","170","XEV_169_170_171","ON","0",null,"Hoofdventiel XEV-169 / 170 / 171 open",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C94-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000180000","180","HOOFDVLAM","ON","0",null,"Hoofdvlam aanwezig",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C95-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000190000","190","XEV_164_165_166","ON","0",null,"Aansteekventielen open",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C96-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000200000","200","XEV_170","ON","0",null,"Hoofdbranders bed 2 uit",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C97-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000210000","210","XEV_171","ON","0",null,"Hoofdbranders bed 1 uit",null,null,"DATETIME","SECTIME","7","BRANDER_M",null,null,"NO",{"$nulls":4},"{7C610C98-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000220000","960","XPV800_STAT","=","0",null,"Verlaadklep XPV-800 geopend",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7C610CA1-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000230000","970","XPV800_STAT","=","3",null,"Verlaadklep XPV-800 gesloten",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7C610CA2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000240000","980","XPV800_RECIR","ON","0",null,"Verlaadklep XPV-800 dicht  (recirculatie)",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7C610CA3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000250000","990","PV1008_STAT","=","0",null,"Snelsluit klep PV-1008 geopend",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7C610CA4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000260000","1000","PV1008_STAT","=","3",null,"Snelsluit klep PV-1008 gesloten",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7C610CA5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000270000","1610","MA160_3_STAT","=","0",null,"Sluis A-160.3 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CB4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000280000","1620","MA160_3_STAT","=","3",null,"Sluis A-160.3 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CB5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000290000","1630","MA160_1_STAT","=","0",null,"Sluis A-160.1 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CB6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000300000","1640","MA160_1_STAT","=","3",null,"Sluis A-160.1 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CB7-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000310000","1650","MA160_2_STAT","=","0",null,"Sluis A-160.2 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CB8-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000320000","1660","MA160_2_STAT","=","3",null,"Sluis A-160.2 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CB9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000330000","1670","MA161_STAT","=","0",null,"Schroef A-161 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CBA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000340000","1680","MA161_STAT","=","3",null,"Schroef A-161 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CBB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000350000","1690","MA162_STAT","=","0",null,"Schroef A-162 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CBC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000360000","1700","MA162_STAT","=","3",null,"Schroef A-162 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CBD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000370000","1750","MA173_STAT","=","0",null,"Pomp P-804 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CC2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000380000","1760","MA173_STAT","=","3",null,"Pomp P-804 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CC3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000390000","1770","MA179_STAT","=","0",null,"Sluis A-179 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CC4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000400000","1780","MA179_STAT","=","3",null,"Sluis A-179 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CC5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000410000","1910","MK151_STAT","=","0",null,"Blower K-151 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000420000","1920","MK151_STAT","=","3",null,"Blower K-151 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000430000","1930","MK152_STAT","=","0",null,"Blower K-152 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000440000","1940","MK152_STAT","=","3",null,"Blower K-152 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000450000","1950","MK910_STAT","=","0",null,"Ventilator K-910 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000460000","1960","MK910_STAT","=","3",null,"Ventilator K-910 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD7-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000470000","1970","MK172_STAT","=","0",null,"Blower K-172 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD8-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000480000","1980","MK172_STAT","=","3",null,"Blower K-172 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CD9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000490000","1990","MK175_STAT","=","0",null,"Blower K-175 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CDA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000500000","2000","MK175_STAT","=","3",null,"Blower K-175 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CDB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000510000","2010","MK151_2_STAT","=","0",null,"Blower K-151.2 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CDC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000520000","2020","MK151_2_STAT","=","3",null,"Blower K-151.2 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CDD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000530000","2030","MP815_2_STAT","=","0",null,"Pomp P-815.2 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CDE-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000540000","2040","MP815_2_STAT","=","3",null,"Pomp P-815.2 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CDF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000550000","2050","MK818_2_STAT","=","0",null,"Blower K-818.2 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE0-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000560000","2060","MK818_2_STAT","=","3",null,"Blower K-818.2 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE1-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000570000","2070","MP910A_STAT","=","0",null,"Pomp P-910A running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000580000","2080","MP910A_STAT","=","3",null,"Pomp P-910A stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000590000","2090","MP910S_STAT","=","0",null,"Pomp P-910S running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000600000","2100","MP910S_STAT","=","3",null,"Pomp P-910S stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000610000","2110","MP950_STAT","=","0",null,"Pomp P-950 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000620000","2120","MP950_STAT","=","3",null,"Pomp P-950 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE7-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000630000","2130","MK818_STAT","=","0",null,"Blower K-818 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE8-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000640000","2140","MK818_STAT","=","3",null,"Blower K-818 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CE9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000650000","2150","MK820A_STAT","=","0",null,"Blower K-820A running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CEA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000660000","2160","MK820A_STAT","=","3",null,"Blower K-820A stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CEB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000670000","2170","MK820B_STAT","=","0",null,"Blower K-820B running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CEC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000680000","2180","MK820B_STAT","=","3",null,"Blower K-820B stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CED-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000690000","2190","MP800_STAT","=","0",null,"Pomp P-800 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CEE-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000700000","2200","MP800_STAT","=","3",null,"Pomp P-800 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CEF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000710000","2210","MP802A_STAT","=","0",null,"Pomp P-802A running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF0-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000720000","2220","MP802A_STAT","=","3",null,"Pomp P-802A stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF1-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000730000","2230","MP805_STAT","=","0",null,"Pomp P-805 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF2-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000740000","2240","MP805_STAT","=","3",null,"Pomp P-805 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF3-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000750000","2250","MP815_STAT","=","0",null,"Pomp P-815 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF4-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000760000","2260","MP815_STAT","=","3",null,"Pomp P-815 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF5-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000770000","2270","MP816A_STAT","=","0",null,"Pomp P-816A running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF6-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000780000","2280","MP816A_STAT","=","3",null,"Pomp P-816A stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF7-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000790000","2290","MP816B_STAT","=","0",null,"Pomp P-816B running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF8-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000800000","2300","MP816B_STAT","=","3",null,"Pomp P-816B stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CF9-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000810000","2310","MP816C_STAT","=","0",null,"Wasmachine running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CFA-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000820000","2320","MP816C_STAT","=","3",null,"Wasmachine stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CFB-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000830000","2330","MP819_STAT","=","0",null,"Pomp P-819 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CFC-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000840000","2340","MP819_STAT","=","3",null,"Pomp P-819 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CFD-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000850000","2350","MM802_STAT","=","0",null,"Roerwerk M-802 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CFE-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000860000","2360","MM802_STAT","=","3",null,"Roerwerk M-802 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610CFF-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000870000","2370","MM804_STAT","=","0",null,"Roerwerk M-804 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610D00-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000880000","2380","MM804_STAT","=","3",null,"Roerwerk M-804 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{7C610D01-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000890000","2420","SEQ5_RUN","ON","0",null,"Sequence 5 - Besturing doekenfilter running",null,null,"DATETIME","SECTIME","9","SEQUENCES",null,null,"NO",{"$nulls":4},"{7C610D04-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000900000","2450","RESET_SEQ5","ON","0",null,"Sequence 5 - Besturing doekenfilter stop",null,null,"DATETIME","SECTIME","9","SEQUENCES",null,null,"NO",{"$nulls":4},"{7C610D07-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000910000","4490","EO_150","ON","0",null,"SEAC - Besturing klepstation beschikbaar",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D08-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000920000","4500","EO_151","ON","0",null,"SEAC - 24VDC beschikbaar",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D09-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000930000","4510","EO_152","ON","0",null,"SEAC - 24VAC beschikbaar",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D0A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000940000","4520","EO_153","ON","0",null,"SEAC - 3 fasen spanning beschikbaar",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D0B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000950000","4530","FO_156_1","ON","0",null,"SEAC - P-156.1 O.K.",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D0C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000960000","4540","FO_156_2","ON","0",null,"SEAC - P-156.2 O.K.",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D0D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000970000","4550","MO_156_1","ON","0",null,"SEAC - P-156.1 aansturing",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D0E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000980000","4560","MO_156_2","ON","0",null,"SEAC - P-156.2 aansturing",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D0F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0000990000","4570","XS_112_1","ON","0",null,"SEAC - XEV-112 lucht, spanning aanwezig",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D10-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001000000","4580","XS_112","ON","0",null,"SEAC - XEV-112 eindstand lucht",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D11-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001010000","4590","XS_113_1","ON","0",null,"SEAC - XEV-113 water, spanning aanwezig",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D12-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001020000","4600","XS_113","OFF","0",null,"SEAC - XEV-113 eindstand water",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D13-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001030000","4610","FI_170",">","30",null,"SEAC - Water injectie gestart",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D14-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001040000","4620","SEAC_SB","ON","0",null,"SEAC - Control system stand-by",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D15-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001050000","4630","LIC815_1_VRIJ","ON","0",null,"Vrijgave niveau regeling LIC-815.1 (quench)",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D16-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001060000","4640","ALLTAGSAUTO","ON","0",null,"Alle motoren, pompen en kleppen in \"AUTO\"",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D17-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001070000","4650","M_200","ON","0",null,"Slib & Sludge Roerwerk M-200 running",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D18-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001080000","4660","M_201","ON","0",null,"Slib & Sludge Roerwerk M-201 running",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D19-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001090000","4670","P_210","ON","0",null,"SLib & Sludge Pomp P-210 running",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D1A-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001100000","4680","XEV_201","ON","0",null,"Slib & Sludge Klep XEV-201 open",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D1B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001110000","4681","XEV_201","OFF","0",null,"Slib & Sludge Klep XEV-211 open",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{69F05F09-0199-11D9-9708-00087440B138}"]
["SHARED","MELD","0001120000","4690","XEV_200","ON","0",null,"Slib & Sludge Klep XEV-200 open",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D1C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001130000","4700","P_210_FREQ","ON","0",null,"Slib & Sludge Storing freq. regelaar P-210",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D1D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001140000","4701","P_210_STOR","ON","0",null,"Slib & Sludge Storing pomp P-210",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{69F05F22-0199-11D9-9708-00087440B138}"]
["SHARED","MELD","0001150000","4710","M_201_STOR","ON","0",null,"Slib & Sludge Storing roerwerk M-201",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D1E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001160000","4720","LSLL_201","ON","0",null,"Slib & Sludge Laag niveau V-201",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D1F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001170000","4730","LSH_201","ON","0",null,"Slib & Sludge Hoog niveau V-201",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D20-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001180000","4740","LSLL_200","ON","0",null,"Slib & Sludge Laag niveau V-200",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D21-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001190000","4750","LSL_200","ON","0",null,"Slib & Sludge Vooralarm laag niveau V-200",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D22-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001200000","4751","LSL_201","ON","0",null,"Slib & Sludge Vooralarm laag niveau V-201",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{69F05F0D-0199-11D9-9708-00087440B138}"]
["SHARED","MELD","0001210000","4760","M_200_STOR","ON","0",null,"Slib & Sludge Storing roerwerk M-200",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D23-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001220000","4780","LSH_200","ON","0",null,"Slib & Sludge Hoog niveau V-200",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D25-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001230000","4790","SLIB_SP","ON","0",null,"Slib & Sludge Spanning aanwezig",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D26-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001240000","4800","TZS_176_O","ON","0",null,"Regelklep TCV-176 geheel open",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D27-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001250000","4810","TZS_176_D","ON","0",null,"Regelklep TCV-176 geheel dicht",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D28-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001260000","4820","LI_802_1","<=","40",null,"Niveau hydroxide vat V-802  < 40 - bestellen",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D29-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001270000","4840","NO_INTERLOCK","ON","0",null,"Geen bypass interlock mogelijk vanuit scada",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D2B-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001280000","4850","NO_INTERLOCK","OFF","0",null,"Sleutelschakelaar bypass interlock bediend",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D2C-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001290000","4860","DOEKHEAT1","ON","0",null,"Verwarming doekenfilter conus 1 in bedrijf",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D2D-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001300000","4870","DOEKHEAT2","ON","0",null,"Verwarming doekenfilter conus 2 in bedrijf",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D2E-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001310000","4875","DOEKHEAT3","ON","0",null,"Verwarming doekenfilter conus 3 in bedrijf",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{38720593-1861-11D9-9708-00087440B138}"]
["SHARED","MELD","0001320000","4880","DOEKHEATKOP","ON","0",null,"Verwarming doekenfilter kop in bedrijf",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D2F-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001330000","4890","VIBRO_R","ON","0",null,"VibroControl MK-151 in bedrijf",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D30-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001340000","4900","NOODVD_STATUS","ON","0",null,"Noodvoeding RTO stand-by",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D31-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001350000","4910","NOODVD_NET","ON","0",null,"Netvoeding noodvoeding RTO aanwezig",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{7C610D32-CEC3-11D6-96CD-00087440B138}"]
["SHARED","MELD","0001360000","5000","XEV162_1_STAT","=","0",null,"Uitvoerklep XEV-162.1 is geopend",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7DB5AD33-3ED4-11D9-9709-00087440B138}"]
["SHARED","MELD","0001370000","5010","XEV162_1_STAT","=","3",null,"Uitvoerklep XEV-162.1 is gesloten",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7DB5AD35-3ED4-11D9-9709-00087440B138}"]
["SHARED","MELD","0001380000","5020","XEV162_2_STAT","=","0",null,"Uitvoerklep XEV-162.2 is geopend",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7DB5AD37-3ED4-11D9-9709-00087440B138}"]
["SHARED","MELD","0001390000","5030","XEV162_2_STAT","=","3",null,"Uitvoerklep XEV-162.2 is gesloten",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7DB5AD39-3ED4-11D9-9709-00087440B138}"]
["SHARED","MELD","0001400000","5040","XEV162_3_STAT","=","0",null,"Uitvoerklep XEV-162.3 is geopend",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7DB5AD3B-3ED4-11D9-9709-00087440B138}"]
["SHARED","MELD","0001410000","5050","XEV162_3_STAT","=","3",null,"Uitvoerklep XEV-162.3 is gesloten",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{7DB5AD3D-3ED4-11D9-9709-00087440B138}"]
["SHARED","MELD","0001420000","1530","MA151_STAT","=","0",null,"Schroef A-151 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D64-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001430000","1540","MA151_STAT","=","3",null,"Schroef A-151 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D65-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001440000","1550","MA152_1_STAT","=","0",null,"Schroef A-152.1 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D68-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001450000","1560","MA152_1_STAT","=","3",null,"Schroef A-152.1 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D69-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001460000","1590","MA152_STAT","=","0",null,"Schroef A-152 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D6C-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001470000","1600","MA152_STAT","=","3",null,"Schroef A-152 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D6D-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001480000","1790","MA182_STAT","=","0",null,"Schroef A-150.1 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D70-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001490000","1800","MA182_STAT","=","3",null,"Schroef A-150.1 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D71-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001500000","1510","MA150_STAT","=","0",null,"Schroef A-150 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D74-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001510000","1520","MA150_STAT","=","3",null,"Schroef A-150 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D75-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001520000","1730","MA168_2_STAT","=","0",null,"Schroef A-151.1 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D78-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001530000","1740","MA168_2_STAT","=","3",null,"Schroef A-151.1 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D79-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001540000","1710","MA153_STAT","=","0",null,"Shredder A-153 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D7C-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001550000","1720","MA153_STAT","=","3",null,"Shredder A-153 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D7D-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001560000","1570","MA157_STAT","=","0",null,"Snelsluitklep XEV-157 open",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D80-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001570000","1580","MA157_STAT","=","3",null,"Snelsluitklep XEV-157 dicht",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D81-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001580000","1890","MK150_STAT","=","0",null,"Blower K-150 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D84-90B7-11D9-9718-00087440B138}"]
["SHARED","MELD","0001590000","1900","MK150_STAT","=","3",null,"Blower K-150 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{66DC7D85-90B7-11D9-9718-00087440B138}"]
["USER","ALARM_RES","0000010000","2680","FAL_912","OFF","0",null,"Lage flow koelwater E-830",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[26]",null,null,"{591FA5C9-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000020000","2480","FSAL_155","OFF","0",null,"Lage flow koelwater P-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[24]",null,null,"{591FA5CB-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000030000","2490","FSAL_156","OFF","0",null,"Lage flow koelwater P-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[25]",null,null,"{591FA5CD-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000040000","4450","SA1_ALARM","OFF","0",null,"Alarm Handling SA1",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5CF-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000050000","4470","SA2_ALARM","OFF","0",null,"Alarm afzuiging oven SA2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5D1-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000060000","1050","MOTOR_AL[18]","ON","0",null,"Blower K-129 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{591FA5D3-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000070000","1070","MOTOR_AL[26]","ON","0",null,"Blower K-134 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{591FA5D5-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000080000","4340","PAH_1003","ON","0",null,"Druk in lans hoog",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5D7-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000090000","4350","PAHH_1003","ON","0",null,"Druk in lans zeer hoog",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5D9-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000100000","1060","MOTOR_AL[19]","ON","0",null,"Filter F-129 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{591FA5DB-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000110000","1080","MOTOR_AL[27]","ON","0",null,"Filter F-134 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{591FA5DD-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000120000","3940","PSAH_819_1","OFF","0",null,"Hoge persdruk ventilator K-819",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5DF-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000130000","4200","PAH_150","ON","0",null,"Hoge druk stoomsysteem",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5E1-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000140000","2880","LAH_151","ON","0",null,"Hoog niveau hoofddrum V-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5E3-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000150000","2960","LAH_153","ON","0",null,"Hoog niveau buffervat V-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5E5-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000160000","2840","LSAH_125","OFF","0",null,"Hoog niveau in bunker B-155",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[14]",null,null,"{591FA5E7-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000170000","2720","LSX102","OFF","0",null,"Hoog niveau in silo B-129",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[1]",null,null,"{591FA5E9-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000180000","2750","LSX105","OFF","0",null,"Hoog niveau in silo B-130",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[4]",null,null,"{591FA5EB-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000190000","2780","LSX113","OFF","0",null,"Hoog niveau in silo B-134",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[9]",null,null,"{591FA5ED-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000200000","2810","LSX116","OFF","0",null,"Hoog niveau in silo B-135",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[12]",null,null,"{591FA5EF-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000210000","3350","LAH_830_1","OFF","0",null,"Hoog niveau in V-830 magnesium filter",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5F1-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000220000","2920","LAH_152","ON","0",null,"Hoog niveau nevendrum V-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5F3-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000230000","4460","SA1_HOOGNIVO","OFF","0",null,"Hoog nivo stofvat Handling SA1",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5F5-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000240000","4480","SA2_HOOGNIVO","OFF","0",null,"Hoog nivo stofvat SA2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5F7-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000250000","4240","XZS_156","OFF","0",null,"Kettingbreuk elevator A-156.2",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[49]",null,null,"{591FA5F9-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000260000","840","KLEPPEN_AL[15]","ON","0",null,"Keuzeklep XPV-108 in alarm",null,null,"DATETIME","SECTIME","7","KLEP_ALARM",null,null,"NO",{"$nulls":4},"{591FA5FB-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000270000","300","FS_155_156","ON","0",null,"Koelwater P-150 / P-151 niet aanwezig",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA5FD-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000280000","2870","LAL_151","ON","0",null,"Laag niveau hoofddrum V-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA5FF-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000290000","2950","LAL_153","ON","0",null,"Laag niveau buffervat V-151",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA601-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000300000","2850","LSAL_126","ON","0",null,"Laag niveau in bunker B-155",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[15]",null,null,"{591FA603-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000310000","2730","LSX103","OFF","0",null,"Laag niveau in silo B-129",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[2]",null,null,"{591FA605-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000320000","2760","LSX106","OFF","0",null,"Laag niveau in silo B-130",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[5]",null,null,"{591FA607-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000330000","2790","LSX114","OFF","0",null,"Laag niveau in silo B-134",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[10]",null,null,"{591FA609-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000340000","2820","LSX117","OFF","0",null,"Laag niveau in silo B-135",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[13]",null,null,"{591FA60B-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000350000","2910","LAL_152","ON","0",null,"Laag niveau nevendrum V-150",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA60D-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000360000","2540","FSAL_165","OFF","0",null,"Lage flow koelwater A-158",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",null,"ALARM_STAT[23]",null,null,"{591FA60F-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000370000","2460","FIC_152","<","7000",null,"Lage flow koelwater bed 1",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA611-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000380000","2470","FIC_153","<","7000",null,"Lage flow koelwater bed 2",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA613-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000390000","2740","LSX104","OFF","0",null,"Silo B-130 vol",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[3]",null,null,"{591FA615-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000400000","2770","LSX112","OFF","0",null,"Silo B-134 vol",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[8]",null,null,"{591FA617-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000410000","2800","LSX115","OFF","0",null,"Silo B-135 vol",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",null,"ALARM_STAT[11]",null,null,"{591FA619-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000420000","260","PSH_151","ON","0",null,"Stoomdruk  >  15.2 te hoog",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA61B-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000430000","4260","TAH_1002","ON","0",null,"Temperatuur in lans hoog",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA61D-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000440000","4270","TAHH_1002","ON","0",null,"Temperatuur in lans zeer hoog",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA61F-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000450000","4360","FS_1007","OFF","0",null,"Waterflow in lans te laag",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA621-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000460000","4250","TI_188",">=","400",null,"Temperatuur KAT invoer  >  400 grd.C",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA623-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000470000","230","FS_152","ON","0",null,"Waterflow naar bedbundel 1  <  minimaal",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA625-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000480000","240","FS_153","ON","0",null,"Waterflow naar bedbundel 2  <  minimaal",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA627-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000490000","250","FS_154","ON","0",null,"Totale waterflow stoomsysteem te laag",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA629-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000500000","1440","MOTOR_AL[87]","ON","0",null,"Trilmotor B-154 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{591FA62B-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000510000","1450","MOTOR_AL[88]","ON","0",null,"Trilmotor B-155 in alarm",null,null,"DATETIME","SECTIME","7","MOTOR_ALARM",null,null,"NO",{"$nulls":4},"{591FA62D-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000520000","3490","TAH_190","ON","0",null,"Hoge temperatuur in bunker B-154",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA62F-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000530000","3510","TAH_191","ON","0",null,"Hoge temperatuur in bunker B-155",null,null,"DATETIME","SECTIME","9","TABLE1",null,null,"NO",{"$nulls":4},"{591FA631-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000540000","3500","TAHH_190","ON","0",null,"Zeer hoge temperatuur in bunker B-154",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA633-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000550000","3520","TAHH_191","ON","0",null,"Zeer hoge temperatuur in bunker B-155",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA635-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000560000","280","LSHH_154","ON","0",null,"Zeer hoog niveau hoofddrum",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA637-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000570000","2970","LAHH_153","ON","0",null,"Zeer hoog niveau buffervat V-151",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA639-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000580000","2890","LAHH_151","ON","0",null,"Zeer hoog niveau hoofddrum V-150",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA63B-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000590000","2930","LAHH_152","ON","0",null,"Zeer hoog niveau nevendrum V-150",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA63D-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000600000","290","LSHH_155","ON","0",null,"Zeer hoog niveau nevendrum",null,null,"DATETIME","SECTIME","7","BRANDER_S",null,null,"NO",{"$nulls":4},"{591FA63F-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000610000","2860","LALL_151","ON","0",null,"Zeer laag niveau hoofddrum V-150",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA641-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000620000","2940","LSLL_153","ON","0",null,"Zeer laag niveau buffervat V-151",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA643-5452-11D9-970A-00087440B138}"]
["USER","ALARM_RES","0000630000","4210","PAHH_150","ON","0",null,"Zeer hoge druk stoomsysteem",null,null,"DATETIME","SECTIME","8","TABLE1",null,null,"NO",{"$nulls":4},"{591FA645-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000010000","500","KET_TRIP[0][0]","ON","0",null,"KETELTRIP - Stoomdruk > 16 bar",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA547-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000020000","510","KET_TRIP[0][1]","ON","0",null,"KETELTRIP - Lage flow koelwater P-150",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA549-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000030000","520","KET_TRIP[0][2]","ON","0",null,"KETELTRIP - Gasvoorw. bed 1",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA54B-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000040000","530","KET_TRIP[0][3]","ON","0",null,"KETELTRIP - Gasvoorw. bed 2",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA54D-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000050000","540","KET_TRIP[0][4]","ON","0",null,"KETELTRIP - Temperatuur bed 1 > 1000 grd.C",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA54F-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000060000","550","KET_TRIP[0][7]","ON","0",null,"KETELTRIP - Lage druk hoofdgas leiding",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA551-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000070000","560","KET_TRIP[0][8]","ON","0",null,"KETELTRIP - Temperatuur bed 2 > 1000 grd.C",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA553-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000080000","570","KET_TRIP[0][9]","ON","0",null,"KETELTRIP - PS_167.1",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA555-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000090000","580","KET_TRIP[0][10]","ON","0",null,"KETELTRIP - dP doekenfilter > 18 mbar",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA557-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000100000","590","KET_TRIP[0][16]","ON","0",null,"KETELTRIP - MK-151 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA559-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000110000","600","KET_TRIP[0][17]","ON","0",null,"KETELTRIP - MK-150 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA55B-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000120000","610","KET_TRIP[0][18]","ON","0",null,"KETELTRIP - Lage flow P-150 naar bedbundel",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA55D-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000130000","620","KET_TRIP[0][19]","ON","0",null,"KETELTRIP - FT-152 < minimaal",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA55F-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000140000","630","KET_TRIP[0][20]","ON","0",null,"KETELTRIP - FT-153 < minimaal",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA561-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000150000","640","KET_TRIP[0][21]","ON","0",null,"KETELTRIP - MP-150 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA563-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000160000","650","KET_TRIP[0][22]","ON","0",null,"KETELTRIP - MK-158 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA565-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000170000","660","KET_TRIP[0][23]","ON","0",null,"KETELTRIP - Bedhoogte < minimaal",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA567-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000180000","670","KET_TRIP[0][24]","ON","0",null,"KETELTRIP - Bedhoogte > maximaal",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA569-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000190000","680","KET_TRIP[0][26]","ON","0",null,"KETELTRIP - Laag niveau hoofddrum (Mobrey)",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA56B-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000200000","690","KET_TRIP[0][27]","ON","0",null,"KETELTRIP - Laag niveau nevendrum (Mobrey)",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA56D-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000210000","700","KET_TRIP[0][28]","ON","0",null,"KETELTRIP - Vuurhaarddruk > max",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA56F-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000220000","710","KET_TRIP[0][30]","ON","0",null,"KETELTRIP - Lage flow koelwater P-151",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA571-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000230000","720","KET_TRIP[0][31]","ON","0",null,"KETELTRIP - Hoge druk hoofdgas leiding",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA573-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000240000","730","KET_TRIP[0][32]","ON","0",null,"KETELTRIP - Temperatuur doekenfilter > 235",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA575-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000250000","740","KET_TRIP[0][33]","ON","0",null,"KETELTRIP - Percentage stof > 25 procent",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA577-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000260000","750","KET_TRIP[0][34]","ON","0",null,"KETELTRIP - Temperatuur na scrubber > 80 grd",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA579-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000270000","760","KET_TRIP[0][35]","ON","0",null,"KETELTRIP - MK-818 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA57B-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000280000","770","KET_TRIP[0][40]","ON","0",null,"KETELTRIP - Lage flow C-816/817/818",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA57D-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000290000","780","KET_TRIP[0][42]","ON","0",null,"KETELTRIP - Hoog alarm SO2 30 minuten",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA57F-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000300000","790","KET_TRIP[0][43]","ON","0",null,"KETELTRIP - MP-816A/B/C niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA581-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000310000","800","KET_TRIP[0][45]","ON","0",null,"KETELTRIP - MA-159 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA583-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000320000","810","KET_TRIP[0][46]","ON","0",null,"KETELTRIP - MA-160.1 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA585-5452-11D9-970A-00087440B138}"]
["USER","KETEL","0000330000","820","KET_TRIP[0][47]","ON","0",null,"KETELTRIP - MA-160.2 niet in bedrijf",null,null,"DATETIME","SECTIME","1","KETELTRIP_ALARM",null,null,"NO",{"$nulls":4},"{591FA587-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000010000","1500","MF134_STAT","=","3",null,"Filter F-134 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6B9-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000020000","1490","MF134_STAT","=","0",null,"Filter F-134 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6BB-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000030000","1470","MF129_STAT","=","0",null,"Filter F-129 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6BD-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000040000","1480","MF129_STAT","=","3",null,"Filter F-129 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6BF-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000050000","1850","MK129_STAT","=","0",null,"Blower K-129 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6C1-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000060000","1860","MK129_STAT","=","3",null,"Blower K-129 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6C3-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000070000","1870","MK134_STAT","=","0",null,"Blower K-134 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6C5-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000080000","1880","MK134_STAT","=","3",null,"Blower K-134 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6C7-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000090000","900","XPV108_STAT","=","0",null,"Keuzeklep XPV-108 naar B-134",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{591FA6C9-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000100000","910","XPV108_STAT","=","3",null,"Keuzeklep XPV-108 naar B-135",null,null,"DATETIME","SECTIME","9","KLEP_STAT",null,null,"NO",{"$nulls":4},"{591FA6CB-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000110000","4770","XEV_833","ON","0",null,"MgSO4 - Klep XEV-833 open",null,null,"DATETIME","SECTIME","9","TABLE2",null,null,"NO",{"$nulls":4},"{591FA6CD-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000120000","2400","SEQ1_RUN","ON","0",null,"Sequence 1 - Laden B129/B130 running",null,null,"DATETIME","SECTIME","9","SEQUENCES",null,null,"NO",{"$nulls":4},"{591FA6CF-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000130000","2410","SEQ2_RUN","ON","0",null,"Sequence 2 - Laden B134/B135 running",null,null,"DATETIME","SECTIME","9","SEQUENCES",null,null,"NO",{"$nulls":4},"{591FA6D1-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000140000","2430","RESETSEQ_1","ON","0",null,"Sequence 1 - Laden B129/B130 stop",null,null,"DATETIME","SECTIME","9","SEQUENCES",null,null,"NO",{"$nulls":4},"{591FA6D3-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000150000","2440","RESETSEQ_2","ON","0",null,"Sequence 2 - Laden B134/B135 stop",null,null,"DATETIME","SECTIME","9","SEQUENCES",null,null,"NO",{"$nulls":4},"{591FA6D5-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000160000","1810","MB154_STAT","=","0",null,"Trilmotor MB-154 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6D7-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000170000","1820","MB154_STAT","=","3",null,"Trilmotor MB-154 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6D9-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000180000","1830","MB155_STAT","=","0",null,"Trilmotor MB-155 running",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6DB-5452-11D9-970A-00087440B138}"]
["USER","MELD_RES","0000190000","1500","MF134_STAT","=","3",null,"Filter F-134 stop",null,null,"DATETIME","SECTIME","9","MOTOR_STAT",null,null,"NO",{"$nulls":4},"{591FA6DD-5452-11D9-970A-00087440B138}"]