{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Blad1","Blad2","Blad3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Blad1","index":0,"n_rows":241,"n_cols":9,"rows_kept":241,"cut":false,"hidden":false,"merged":[[0,0,0,8],[54,0,54,8],[85,0,85,8]],"flags":["formulas_cached_only"]}
["Analoge ingangen DB-150"]
["stand","Code","Beschrijving","PW","Scaling","0-20","4-20","draads","Opmerking"]
[]
["gaat vervallen","LI-151","Nivo hoofddrum V-150"]
["gaat vervallen","LI-152","Nivo nevendrum V-150"]
["gaat vervallen","LI-153","Nivo buffervat V-151"]
["ok","LI-167","Nivo katbunker B-150","PW-136","0-100",null,"X",2]
["ok","LI-168","Nivo katbunker B-151","PW-138","0-100",null,"X",2,"ander signaal"]
["ok","FI-150","slib en sludge naar bed 1","PW-144","0-1200","X",null,2,"meetkop 4 - 20 mA"]
["ok","FI-151","slib en sludge naar bed 2","PW-146","0-995","X",null,2,"meetkop 4 - 20 mA"]
["gaat vervallen","FIC-152","waterstroom regeling sectie 1","PW-148"]
["gaat vervallen","FIC-153","waterstroom regeling sectie 2","PW-150"]
["ok","QI-157","O2 meting uitgang RTO","PW-152","-6,2 - 25 %",null,"X"]
["ok","FI-816","flow indicatie uitgang waskolom C-816","PW-158","0 - 560 M3/h","X",null,null,"in veld 4- 20 mA (omvormer)"]
["ok","FI-817","flow indicatie uitgang waskolom C-817","PW-160","0 - 560 M3/h","X",null,null,"in veld 4- 20 mA (omvormer)"]
["ok","FI-818","flow indicatie uitgang waskolom C-818","PW-162","0 - 560 M3/h","X",null,null,"Omvormer is eruit in PLC omgezet"]
["ok","LI-800.1","Level indicator producttank V-800","PW-164","0 - 100 %","X"]
["ok","FI-171","gas naar bed 1","PW-166","4,89 - 250 m3/h","X"]
["ok","FI-172","gas naar bed 2","PW-168","4,89 - 250 m3/h","X"]
["ok","FI-176","Spoellucht naar branders","PW-172","0 - 260 m3/h","X"]
["ok","PI-920.3","Druk doekenfilter 3","PW-176","-2,5 - 10 Bar","X"]
["ok","dPI-156","druk indicatie roosterplaat bed 1","PW-178","0 - 150 mBar","X"]
["ok","dPI-157","druk indicatie bedhoogtemeting","PW-180","0-50","X",null,null,"niet in scada"]
["ok","dPI-158","druk indicatie bedhoogtemeting","PW-182","0-50","X",null,null,"niet in scada"]
["ok","dPI-159","druk indicatie bedhoogtemeting","PW-184","0-50","X",null,null,"niet in scada"]
["ok","dPI-160","druk indicatie bed 1 en bed 2 (bedhoogte meting)","PW-186","0-150 cm","X"]
["ok","dPI-161","verschuildruk over bed 2","PW-188","0-150 mBar","X"]
["ok","dPI-162","druk indicatie oven","PW-190","-9,98 - 10 mBar","X"]
["ok","dPI-165","verschildruk meting sproeikoeler","PW-192","-12,5 - 50 Mbar","X",null,null,"PLC gecorrigeerd door scaling"]
["ok","dPI-166","verschildruk meting doekenfilter","PW-194","0,3 t/m 20 mBar","X"]
["is vervallen","SI-150","toerental indicatie schroef A-150","PW-208"]
["is vervallen","SI-151","toerental indicatie schroef A-151","PW-210"]
["ok","QI-151","stofmeting na doekenfilter","PW-214","-6,4 - 100 %","X"]
["is vervallen","NI-150","vermogens meting K-150","PW-218","0 - 100 %"]
["is vervallen","NI-151","vermogens meting K-151","PW-220","0 - 100 %"]
["ok","QI-820.2","dichtheidsmeting V-820","PW-230","1125 - 1380 Kg/m3","X"]
["ok","LI-802.1","nivo indicatie Mg(OH)2 opslagtank","PW-240","0 - 100 %","X"]
["ok","LI-804.1","nivo indicatie final oxidation tank","PW-242","0 - 100 %","X"]
["ok","LI-820.1","nivo indicatie pre oxidatie tank V-820","PW-246","0 - 100 %",null,"X"]
["ok","LI-170","nivo indicatie vat V-156 (SEAC)","PW-244","0 - 100 %",null,"X"]
["ok","PI-812","druk indicatie RG koeler Z-815","PW-248","-100 - +100 mBar","X",null,null,"meetkop 4 - 20 mA (omvormer)"]
["ok","QI-811.1","SO2 in rookgassen naar stack","PW-250","0 - 1000 ppm","X",null,null,"SO2 aardlek van 6 A naar 16 A"]
["ok","FIC-159","flow regeling verbrandingslucht op oven",{"$nulls":5},"is optel van FI-158 en FI-159"]
["is vervallen","TI_gem_act","actuele gemiddelde temperatuur bed 1 en 2"]
["gaat vervallen","FI-152_153","totale waterflow naar bedbundel"]
["ok","QI-816","pH indicatie waskolom C-816","PW-142 / PW-174","2 - 12 pH",null,"X"]
["ok","QI-817","pH indicatie waskolom C-817","PW-200 / PW-252","2 - 12 pH",null,"X"]
["ok","QI-818","pH indicatie waskolom C-818","PW-254 / PW-196","2 - 12 pH",null,"X"]
["ok","QI-819","pH indicatie post ox V-819","PW-198 / PW-224","2 - 12 pH",null,"X",null,"in de fabriek QT-819b niet goed na L4-110/111"]
["ok","QI-820.1","pH indicatie pre ox V-820","PW-226 / PW-228","2 - 12 pH",null,"X"]
["ok","QI-811.1","QI-811.1 in mg/Nm3","PW-250","0 - 2850 mg/Nm3","X"]
[]
[]
[]
["Analoge ingangen DB-151"]
["stand","Code","Beschrijving","PW","Scaling","0-20","4-20","draads","Opmerking"]
["???","FI-170","seac water flow naar C-150","PW-212","0 - 3000 l/h","X",null,null,"in veld waarschijnlijk niet goed"]
["ok","LI-800.4","nivo detectie V-800b","QW-4","60 - 100 %",null,"X"]
["ok","PI-918","druk indicatie perslucht naar doekenfilter","QW-6","0 - 9 Bar",null,"X",4]
["ok","LI-913","nivo in V-950 sealwater","QW-8","0 - 100 %",null,"X",3,"in veld niet ok (verkeerd aangesloten)"]
["ok","PI-919","werkluchtdruk compressor K-172","QW-14","-2,5 - 7,5 Bar",null,"X",null,"blijft in veld niet aangesloten op rangeerverdeler ok"]
["ok","LI-815.1","nivo indicator schrubber C-815","QW-18","0 - 100 %",null,"X"]
["ok","SI-818","frequentie K-818"," QW-122 + PW-134","0 - 60 HZ"]
["ok","FI-158","flow indicator luchttoevoer bed 2","QW-40","0 - 6200 Nm3/h",null,"X",null,"is veranderd op scada in bed 1"]
["ok","FI-159","flow indicator luchttoevoer bed 1","QW-42","0 - 6200 Nm3/h",null,"X",null,"is veranderd op scada in bed 2"]
["ok","TI-804","Temperatuur indicatie V-804","QW-48 + QW-50","0 - 2765 °C",null,null,"PT-100","was QW-48 is nu 48 en 50 i.v.m. PT-100"]
["ok","TI-813","temperatuur indicatie uitvoer schrubber C-815","QW-52 + QW-54","0 - 2765 °C",null,null,"PT-100","was QW-52 is nu 52 en 54 i.v.m. PT-100"]
["ok","TIC-910","temperatuur indicatie koelwaterbak V-910","QW-56 + QW-58","0 - 2765 °C",null,null,"PT-100","was QW-54 is nu 56 en 58 i.v.m. PT-100"]
["ok","TI-147","temperatuur kop doekenfilter","QW-64","0 - 250 °C"]
["ok","TI-148","temperatuur inlaat K-151","QW-66","0 - 250 °C"]
["gaat vervallen","LIC-150","nivo condensor E-151"]
["ok","TI-171","temperatuur van inlaat C-150","QW-82","0 - 1200 °C",null,"X"]
["ok","QI-150","zuurstofmeter in rookgas voor doekenfilter","QW-84","0 - 25 %",null,"X"]
["ok","TI-172","temperatuur indicatie uitlaat C-150","QW-86","0 - 400 °C",null,"X"]
["is vervallen","LI-970","niveau in stikstoftank V-970"]
["is vervallen","PI-970","druk indicatie drukvat V-172"]
["is vervallen","TI-1002","temperatuur verf in leiding na oven"]
["is vervallen","PI-1003","persdruk pomp P-1001 (0-16 Bar)"]
["is vervallen","TI-1004","temperatuur binnen in verfbunker"]
["is vervallen","TI-1005","temperatuur wand verfbunker"]
["is vervallen","TI-1006","temperatuur wand verfbunker"]
["ok","PI-920.1","druk doekenfilter 1","PW-106","0 - 16 bar",null,"X",null,"L4 - 337 en 338"]
["ok","PI-920.2","druk doekenfilter 2","PW-108","0 - 10 bar",null,"X",null,"L4 - 339 en 340"]
["ok","MK-151 speed","frequentie K-151.1 en 2","QW-110 / QW-20","0 - 35 HZ","X + X",null,null,"QW-20 is nog niet aangesloten op K-151.2 in het veld. K-151.1 moet eerst gestart worden."]
[]
["Analoge ingangen DB-152"]
["stand","Code","Beschrijving","PW","Scaling","0-20","4-20","draads","Opmerking"]
["niet aangesloten","TI-150","temp natte kat systeem","QW-128","0 - 1372 °C"]
["ok","TI-151","temp uitlaat RTO","QW-130","0 - 1372 °C"]
["niet aangesloten","TI-152","temp B-153","QW-132"]
["niet aangesloten","TI-154","temp B-162","QW-136"]
["ok","TI-158.2","temp bed 1 boven","QW-138","0 - 1372 °C"]
["ok","TI-149.4","temp perslucht voorverwarmer","QW-140","0 - 1372 °C"]
["ok","TI-160.2","temp bed 1 onder","QW-142","0 - 1372 °C"]
["ok","TI-159.2","temp bed 2 boven","QW-144","0 - 1372 °C"]
["ok","TI-159.3","????","QW-146","0 - 1372 °C",null,null,null,"alleen in trending zichtbaar"]
["ok","TI-161.2","temp bed 2 onder","QW-148","0 - 1372 °C"]
["ok","TI-162.1","temp aansteekbranders","QW-150","-30 - 1372°C"]
["ok","TI-188","????","QW-152",{"$nulls":4},"alleen in trending zichtbaar"]
["ok","TI-163.1","temp freeboard","QW-154","-30 - 1372°C"]
["ok","TI-164","temp steenbekleding","QW-156","0 - 1372 °C"]
["ok","TI-165.1","temp uitlaat oven","QW-158 / QW-184","0 - 1372 °C"]
["ok","TI-167","temp inlaat verbrandingslucht ventilator","QW-160","0 - 1372 °C"]
["is vervallen","TI-168","temp verbrandingslucht naar bed 1 en 2","QW-162"]
["niet aangesloten","TI-157","temperatuur na A-173","QW-84","0 - 1372 °C"]
["spare","TI-181","temperatuur in cycloon","QW-172","0 - 1372 °C"]
["spare","TI-166 oud",null,"QW-174","0 - 1372 °C"]
["ok","TI-186","temp B-150 onder","QW-176","0 - 1372 °C"]
["ok","TI-187","temp B-151 onder","QW-178","0 - 1372 °C"]
["???","TI-301","temp ingang K-151"]
["ok","TIC-176","Temp samsonklep","QW-186","-30 - 1372°C"]
["vervallen","TI-190","temp buffervat V-154","QW-188","0 - 1372 °C",null,null,null,"allen in trending zichtbaar"]
["vervallen","TI-191","temp buffervat V-155","QW-190","0 - 1372 °C",null,null,null,"allen in trending zichtbaar"]
["ok","TI-192","temp B-150 midden","QW-192","0 - 1372 °C"]
["ok","TI-193","temp B-150 boven","QW-194","0 - 1372 °C"]
["ok","TI-194","temp B-151 midden","QW-196","0 - 1372 °C"]
["ok","TI-195","temp B-151 boven","QW-198","0 - 1372 °C"]
["ok","TI-149.2","temp doekenfilterkast 2","QW-208","0 - 1372 °C"]
["ok","TI-149.3","temp doekenfilterkast 3","QW-210","0 - 1372 °C"]
["ok","TI-166","temp voor doekenfilter","QW-174","0 - 1372 °C"]
["ok","TI-149.1","temp doekenfilterkast 1","QW-214","0 - 1372 °C"]
[]
["stand","Code","Beschrijving","PW","Scaling","0-20","4-20","draads","Opmerking"]
["REK 3 KAART 14","L4-145","ANALOGE UITGANGEN"]
["LCV-150","L4-146","LCV-150","PW128-","100 - 0","X"]
["LCV-150","L4-147","LCV-150","PW128+"]
["LCV-151","L4-148","LCV-151","PW130-","0 - 100","X"]
["LCV-151","L4-149","LCV-151","PW130+"]
["LCV-152","L4-150","LCV-152","PW132-","0 - 100","X"]
["LCV-152","L4-151","LCV-152","PW132+"]
["KLEPSTURING FCV-152 WATERSTR. SECTIE 1","L4-152","terugkoppeling frequentie omvormer K-818.2","PW134-","0 - 100","X"]
["KLEPSTURING FCV-152 WATERSTR. SECTIE 1","L4-153","terugkoppeling frequentie omvormer K-818.2","PW134+"]
[";","L4-154",null,";",";"]
[null,"L4-155",null,"PW136-"]
[null,"L4-156",null,"PW136+"]
["PCV-162","L4-157","PCV-162","PW138-","0 - 100","X"]
["PCV-162","L4-158","PCV-162","PW138+"]
["SC-150 (A-150)","L4-159","SC-150 (A-150)","PW140-","0 - 100","X"]
["SC-150 (A-150)","L4-160","SC-150 (A-150)","PW140+"]
["SC-151 (A-151)","L4-161","SC-151 (A-151)","PW142-","0 - 100","X"]
["SC-151 (A-151)","L4-162","SC-151 (A-151)","PW142+"]
["REK 3 KAART 15","L4-163","ANALOGE UITGANGEN","PW","Scaling","0-20","4-20","draads","Opmerking"]
["FCV-153","L4-164","FCV-153","PW144-","100 - 0","X",null,null,"SPEED MA152"]
["FCV-153","L4-165","FCV-153","PW144+",{"$nulls":4},"SPEED MA152"]
["TCV-183","L4-166","TCV-183","PW146-","0 - 100","X",null,null,"SPEED MA153"]
["TCV-183","L4-167","TCV-183","PW146+",{"$nulls":4},"SPEED MA153"]
["TCV-184","L4-168","TCV-184","PW148-","0 - 100","X"]
["TCV-184","L4-169","TCV-184","PW148+"]
["TCV-910","L4-170","TCV-910","PW150-","0 - 200","X",null,null,"KLEPSTURING TCV-182 TEMP. NA LUVO 2"]
["TCV-910","L4-171","TCV-910","PW150+",{"$nulls":4},"KLEPSTURING TCV-182 TEMP. NA LUVO 2"]
[";","L4-172",null,";",";"]
["SPEED MK150  ","L4-173","SC-154","PW152-","0 - 100","X"]
["SPEED MK150  ","L4-174","SC-154","PW152+"]
["SPEED MK158","L4-175","SC-155 / PIC-150","PW154-","0 - 100","X"]
["SPEED MK158","L4-176","SC-155 / PIC-150","PW154+"]
["LIC-815.1","L4-177","LIC-815.1","PW156-","0 - 100","X"]
["LIC-815.1","L4-178","LIC-815.1","PW156+"]
["LIC-804.1","L4-179","LIC-804.1","PW158-","0 - 100","X"]
["LIC-804.1","L4-180","LIC-804.1","PW158+"]
["REK 3 KAART 16","L4-181","ANALOGE UITGANGEN","PW","Scaling","0-20","4-20","draads","Opmerking"]
["dPIC-160","L4-182","SPEED MA158","PW160+","0 - 100","X"]
["dPIC-160","L4-183","SPEED MA158","PW160-"]
["LCV-170","L4-184","LCV-170","PW162+","0 - 100","X"]
["LCV-170","L4-185","LCV-170","PW162-"]
["XXXXXXXXXX","L4-186",null,"PW164+"]
["XXXXXXXXXX","L4-187",null,"PW164-"]
["QIC-816","L4-188","QIC-816","PW166+","0 - 100","X"]
["QIC-816","L4-189","QIC-816","PW166-"]
[";","L4-190",null,";",";"]
["XXXXXXXXXX","L4-191",null,"PW168-"]
["XXXXXXXXXX","L4-192",null,"PW168+"]
["XXXXXXXXXX","L4-193",null,"PW170-"]
["XXXXXXXXXX","L4-194",null,"PW170+"]
["QIC-817","L4-195","QIC-817","PW172-","0 - 100","X"]
["QIC-817","L4-196","QIC-817","PW172+"]
["TCV170","L4-197","TCV170","PW174-","0 - 400","X",null,null,"SETPOINT C-150"]
["TCV170","L4-198","TCV170","PW174+",{"$nulls":4},"SETPOINT C-150"]
["REK 3 KAART 17","L4-199","ANALOGE UITGANGEN","PW","Scaling","0-20","4-20","draads","Opmerking"]
["QCV-818","L4-200","QCV-818","PW176-","0 - 100","X"]
["QCV-818","L4-201","QCV-818","PW176+"]
["QCV-819","L4-202","QCV-819","PW178-","0 - 100","X"]
["QCV-819","L4-203","QCV-819","PW178+"]
["XXXXXXXXXX","L4-204",null,"PW180-"]
["XXXXXXXXXX","L4-205",null,"PW180+"]
["XXXXXXXXXX","L4-206",null,"PW182-"]
["XXXXXXXXXX","L4-207",null,"PW182+"]
[";","L4-208",null,";",";"]
["QCV820-1","L4-209","QCV820-1","PW184-","0 - 100","X"]
["QCV820-1","L4-210","QCV820-1","PW184+"]
["QCV820-2","L4-211","QCV820-2","PW186-","0 - 100","X"]
["QCV820-2","L4-212","QCV820-2","PW186+"]
["TCV-176","L4-213","TCV-176","PW188-","0 of 100"]
["TCV-176","L4-214","TCV-176","PW188+"]
["XXXXXXXXXX","L4-215",null,"PW190-"]
["XXXXXXXXXX","L4-216",null,"PW190+"]
[null,"L4-409","REK 3 KAART 18","PW","Scaling","0-20","4-20","draads","Opmerking"]
["XXXXXXXXXX","L4-410",null,"PW192-"]
["XXXXXXXXXX","L4-411",null,"PW192+"]
["XXXXXXXXXX","L4-412",null,"PW194-"]
["XXXXXXXXXX","L4-413",null,"PW194+"]
["TIC-147","L4-414","TIC-147","PW196-","0 - 100"]
["TIC-147","L4-415","TIC-147","PW196+"]
["PIC-812","L4-416","PIC-812","PW198-","0 - 100"]
["PIC-812","L4-417","PIC-812","PW198+"]
[null,"L4-418"]
["SIC-153","L4-419","SIC-153","PW200-","-12,5 - 50"]
["SIC-153","L4-420","SIC-153","PW200+"]
[null,"L4-421"]
[null,"L4-422"]
[null,"L4-423"]
[null,"L4-424"]
[null,"L4-425"]
[null,"L4-426"]
[null,"L4-427"]
[null,"L4-428"]
[null,"L4-429"]
[]
[]
[]
[null,null,"Lampjes PLC ruimte die niet branden"]
[null,null,"F-800.2"]
[null,null,"F-800.5"]
[null,null,"F-800.7"]
[null,null,"F-814.2"]
[null,null,"F-815.5"]
[null,null,"F-816a"]
[null,null,"F-816b"]
[null,null,"F-817a"]
[null,null,"F-817b"]
[null,null,"F-818  "]
[null,null,"F-818.4"]
[null,null,"F-818a"]
[null,null,"F-818b"]
[null,null,"F-819a"]
[null,null,"F-819b"]
[null,null,"F-820.2"]
[null,null,"F-820.6"]
[null,null,"F-820a"]
[null,null,"F-820b"]
[null,null,"F-908  "]
[null,null,"F-913.1"]

{"sheet":"Blad2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Blad3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}