{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Blad1","Blad2","Blad3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Blad1","index":0,"n_rows":1488,"n_cols":9,"rows_kept":1488,"cut":false,"hidden":false,"merged":[[0,0,0,1],[7,6,7,8],[1341,0,1341,1],[8,2,10,2],[8,0,10,1],[9,8,9,10],[10,8,10,10],[6,0,6,1],[7,0,7,1],[532,0,532,1],[8,6,10,6],[531,3,532,3],[531,0,531,1],[1340,0,1340,1],[8,4,10,4],[8,3,10,3],[8,5,10,5]],"flags":["formulas_cached_only"]}
["P.HOLWEG",null,"VOORBEELD: Ingang 0.0 (PLC Rek 2,Kaart 1,"]
["2006-02-10",null,"Aansluitnummer 4) is op onze rangeerverdeler"]
[null,"24 X 8 ANALOGE INGANGEN.","aangesloten op LIJST 8 - KLEM 2."]
[null,"5 X 8   ANALOGE UITGANGEN","Hiervoor is adernummer 2 van kabel 393 gebruikt."]
[null,"13 X 32 DIGITALE INGANGEN"]
[null,"5 X 32 DIGITALE UITGANGEN"]
["xxxx SYMBOLIEK FILE VOOR MOXBA METREX  xxxxx"]
["xxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxxx",{"$nulls":5},"TEKENINGNUMMER"]
["INGANGEN 13 KAARTEN A 32 INGANGEN ",null,"Na diverse aanpassingen of verwijderingen","HLRVD","R\\K\\Aans","FUNCTIE","KABEL\\NR"]
[{"$nulls":7}," ","GEBRUIKTE IN EN UIT-"]
[{"$nulls":8},"GANGEN IN PROGRAMMA"]
[null,null,null,"L8-1","2\\1\\3","24VDC","393\\1",null,"A 0.0"]
["E 0.0 ","LS123 H NIVO B154 "," ----SPARE------- ","L8-2","2\\1\\4",null,"393\\2",null,"A 0.1"]
["E 0.1 "," ----SPARE------- "," ----SPARE------- ","L8-3","2\\1\\5",null,"393\\3",null,"A 0.2"]
["E 0.2","LS124 L NIVO B154 "," ----SPARE------- ","L8-4","2\\1\\6",null,"393\\4",null,"A 0.5"]
["E 0.3","MK802 CONTACTOR FEEDBACK"," ----SPARE------- ","L8-5","2\\1\\7",null,"393\\5",null,"A 1.0"]
["E 0.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-6","2\\1\\8",null,"393\\6",null,"A 1.1"]
["E 0.5","MA802 CONTACTOR FEEDBACK","xxxxxxxxxxxxxxxx ","L8-7","2\\1\\9",null,"393\\7",null,"A 1.6"]
["E 0.6","LS125 H NIVO B155 "," ----SPARE------- ","L8-8","2\\1\\10",null,"393\\8",null,"A 1.7"]
["E 0.7"," ----SPARE------- "," ----SPARE------- ","L8-9","2\\1\\11",null,"393\\9",null,"A 2.0"]
[";",";",null,"L8-10 ","2\\1\\12",null,"393\\10",null,"A 2.1"]
["E 1.0","MK129 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-11","2\\1\\13",null,"393\\11",null,"A 3.1"]
["E 1.1","MF129 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-12","2\\1\\14",null,"393\\12",null,"A 3.2"]
["E 1.2","VERWARMING 1 DOEKENFILTER IN BEDRIJF ","VERWARMING 1 DOEKENFILTER IN BEDRIJF ","L8-13","2\\1\\15",null,"393\\13",null,"A 3.3"]
["E 1.3","MA130 CONTACTOR FEEDBACK","VERWARMING 2 DOEKENFILTER IN BEDRIJF ","L8-14","2\\1\\16",null,"393\\14",null,"A 3.4"]
["E 1.4","MK132 CONTACTOR FEEDBACK","VERWARMING KOP DOEKENFILTER IN BEDRIJF ","L8-15","2\\1\\17",null,"393\\15",null,"A 3.5"]
["E 1.5"," ----SPARE------- "," ----SPARE------- ","L8-16","2\\1\\18",null,"393\\16",null,"A 3.6"]
["E 1.6","MA128 CONTACTOR FEEDBACK (Q6514)"," ----SPARE------- ","L8-17","2\\1\\19",null,"393\\17",null,"A 3.7"]
["E 1.7","MA131 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-18","2\\1\\20",null,"393\\18",null,"A 4.0"]
[";",";",";","L8-19","2\\1\\21","GND","393\\19",null,"A 4.1"]
[";",";",";","L8-20","2\\1\\22",null,"393\\20",null,"A 4.2"]
[";",";",";","L8-21","2\\1\\23",null,"393\\21",null,"A 4.3"]
[";",";",";","L8-22","2\\1\\24",null,"393\\22",null,"A 4.4"]
["E 2.0","MK134 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-23","2\\1\\25",null,"393\\23",null,"A 4.5"]
["E 2.1","MF134 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-24","2\\1\\26",null,"393\\24",null,"A 5.0"]
["E 2.2","F818-5(24VDC) IFM818.1","INBEDRIJF VIBROCONTROL MK818.1","L8-25","2\\1\\27",null,"393\\25","MK818-2","A 5.1"]
["E 2.3","MA135 CONTACTOR FEEDBACK","H ALARM   VIBROCONTROL MK818.1","L8-26","2\\1\\28",null,"393\\26","MK818-2","A 5.3"]
["E 2.4","HH ALARM VIBROCONTROL MK818 ","HH ALARM VIBROCONTROL MK818.1","L8-27","2\\1\\29",null,"393\\27","MK818-2","A 5.4"]
["E 2.5"," ----SPARE------- "," ----SPARE------- ","L8-28","2\\1\\30",null,"393\\28",null,"A 5.5"]
["E 2.6","MA137 CONTACTOR FEEDBACK","H ALARM VIBROCONTROL MK818.2","L8-29","2\\1\\31",null,"393\\29",null,"A 5.6"]
["E 2.7","MA133 CONTACTOR FEEDBACK","HH ALARM VIBROCONTROL MK818.2","L8-30","2\\1\\32",null,"393\\30",null,"A 5.7"]
[";",";",";","L8-31","2\\1\\33",null,"393\\31",null,"A 6.0"]
["E 3.0","MA140 CONTACTOR FEEDBACK"," ----SPARE------- ","L8-32 ","2\\1\\34",null,"393\\32",null,"A 6.1"]
["E 3.1","MA136 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-33","2\\1\\35",null,"393\\33",null,"A 6.5"]
["E 3.2","MK128 CONTACTOR FEEDBACK (Q6614)"," ----SPARE------- ","L8-34","2\\1\\36",null,"393\\34",null,"A 6.6"]
["E 3.3","MK131 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-35","2\\1\\37",null,"393\\35",null,"A 6.7"]
["E 3.4","LS126 L NIVO B155 "," ----SPARE------- ","L8-36","2\\1\\38",null,"393\\36",null,"A 7.0"]
["E 3.5","LS910 L NIVO V910 ","LS910 L NIVO V910","L8-37","2\\1\\39",null,"393\\37",null,"A 7.1"]
["E 3.6","LS910 LL NIVO V910 ","LS910 LL NIVO V910","L8-38","2\\1\\40",null,"393\\38",null,"A 7.2"]
["E 3.7","MB154 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-39","2\\1\\41",null,"393\\39",null,"A 7.3"]
[null,";",";","L8-40","2\\1\\42 ",null,"393\\PE",null,"A 7.5"]
[";",";",";","L8-41","2\\2\\3","24VDC","394\\1",null,"A 7.6"]
["E 4.0","MB155 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-42","2\\2\\4",null,"394\\2",null,"A 7.7"]
["E 4.1","PULS KETTING MA156.2 ",null,"L8-43","2\\2\\5",null,"394\\3",null,"A 8.0"]
["E 4.2","H ALARM VIBROCONTROL MK151 ","H ALARM VIBROCONTROL MK151.1","L8-44","2\\2\\6",null,"394\\4",null,"A 8.1"]
["E 4.3","HH ALARM VIBROCONTROL MK151 ","HH ALARM VIBROCONTROL MK151.1","L8-45","2\\2\\7",null,"394\\5",null,"A 8.2"]
["E 4.4","XZS104-1 XPV104 NAAR B129 "," ----SPARE------- ","L8-46","2\\2\\8",null,"394\\6",null,"A 8.3"]
["E 4.5","XZS108-1 XPV108 NAAR B134 "," ----SPARE------- ","L8-47","2\\2\\9",null,"394\\7",null,"A 8.5"]
["E 4.6","INBEDRIJF VIBROCONTROL MK151","INBEDRIJF VIBROCONTROL MK151.1","L8-48","2\\2\\10",null,"394\\8",null,"A 8.6"]
["E 4.7","XZS105 EXPLOSIE LUIK OPEN ","XZS105 EXPLOSIE LUIK OPEN ","L8-49","2\\2\\11",null,"394\\9",null,"A 8.7"]
[";",";",";","L8-50","2\\2\\12",null,"394\\10",null,"A 9.0"]
["E 5.0","LS 300 NIVOMELDING DOEKENFILTER","LS920 NIVOMELDING DOEKENFILTER 1","L8-51","2\\2\\13",null,"394\\11",null,"A 9.3"]
["E 5.1","TRACING MK151 IN BEDRIJF ","TRACING ZUIGLEIDING MK151.1 EN 2  IN BEDRIJF ","L8-52","2\\2\\14",null,"394\\12",null,"A 9.4"]
["E 5.2"," ----SPARE------- "," ----SPARE------- ","L8-53","2\\2\\15",null,"394\\13",null,"A 9.5"]
["E 5.3","KLEP XEV-109 DICHT","xxxxxxxxxxxxxxxx ","L8-54","2\\2\\16",null,"394/14",null,"A 9.6"]
["E 5.4","XZS104-2 XPV104 NAAR B130 "," ----SPARE------- ","L8-55","2\\2\\17",null,"394\\15",null,"A 9.7"]
["E 5.5","XZS108-2 XPV108 NAAR B135 "," ----SPARE------- ","L8-56","2\\2\\18",null,"394\\16",null,"A 10.3"]
["E 5.6","MP950 CONTACTOR FEEDBACK ","MP950 CONTACTOR FEEDBACK ","L8-57","2\\2\\19",null,"394\\17",null,"A 10.4"]
["E 5.7","dPAH818-8 SPROEIPLAAT C818 HOOG ","dPAH818-8 SPROEIPLAAT C818 HOOG ","L8-58","2\\2\\20",null,"394\\18",null,"A 10.5"]
[";",";",";","L8-59","2\\2\\21","GND","394\\19",null,"A 10.6"]
[";",";",";","L8-60","2\\2\\22",null,"394\\20",null,"A 11.0"]
[";",";",";","L8-61","2\\2\\23",null,"394\\21",null,"A 11.1"]
[";",";",";","L8-62","2\\2\\24",null,"394\\22",null,"A 11.4"]
["E 6.0","LS801 L NIVO B801","KLEP XEV 162.1 OPEN","L8-63","2\\2\\25",null,"394\\23",null,"A 11.5"]
["E 6.1","LS802 L NIVO B801","KLEP XEV 162.1 DICHT","L8-64","2\\2\\26",null,"394\\24",null,"A 12.0"]
["E 6.2","LS803 LL NIVO B801","KLEP XEV 162.2 OPEN","L8-65","2\\2\\27",null,"394\\25",null,"A 12.5"]
["E 6.3","LS804 HH NIVO B801","KLEP XEV 162.2 DICHT","L8-66","2\\2\\28",null,"394\\26",null,"A 12.6"]
["E 6.4","LS805 H NIVO B801","KLEP XEV 162.3 OPEN","L8-67","2\\2\\29",null,"394\\27",null,"A 12.7"]
["E 6.5","LS806 L NIVO B802","KLEP XEV 162.3 DICHT","L8-68","2\\2\\30",null,"394\\28",null,"A 13.1"]
["E 6.6","LS107 H NIVO B131","xxxxxxxxxxxxxxxx ","L8-69","2\\2\\31",null,"394\\29",null,"A 13.2"]
["E 6.7","LS118 H NIVO B163 ","LS118 H NIVO B163","L8-70","2\\2\\32",null,"394\\30",null,"A 13.3"]
[";",";",";","L8-71","2\\2\\33",null,"394\\31",null,"A 13.4"]
["E 7.0","LS101 HH NIVO B129 ","UITVOERKLEP XEV-162.3 DOEKENFILTER DICHT","L8-72","2\\2\\34",null,"394\\32",null,"A 13.5"]
["E 7.1","LS104 HH NIVO B130 "," ----SPARE------- ","L8-73","2\\2\\35",null,"394\\33",null,"A 13.6"]
["E 7.2","LS112 HH NIVO B134 "," ----SPARE------- ","L8-74","2\\2\\36",null,"394\\34",null,"A 13.7"]
["E 7.3","LS115 HH NIVO B135 "," ----SPARE------- ","L8-75","2\\2\\37",null,"394\\35",null,"A 14.0"]
["E 7.4","LS102 H NIVO B129 ","TRACING CONUS DOEKENFILTER 3","L8-76","2\\2\\38",null,"394\\36",null,"A 14.1"]
["E 7.5","LS105 H NIVO B130 "," ----SPARE------- ","L8-77","2\\2\\39",null,"394\\37",null,"A 14.2"]
["E 7.6","LS113 H NIVO B134 "," ----SPARE------- ","L8-78","2\\2\\40",null,"394\\38",null,"A 14.3"]
["E 7.7","LS116 H NIVO B135 "," ----SPARE------- ","L8-79","2\\2\\41",null,"394\\39",null,"A 14.4"]
[";",";",";","L8-80","2\\2\\42",null,"394\\PE",null,"A 14.5"]
[";",";",";","L8-81","2\\3\\3","24VDC","395\\1",null,"A 14.6"]
["E 8.0","LS103 L NIVO B129 "," ----SPARE------- ","L8-82","2\\3\\4",null,"395\\2",null,"A 14.7"]
["E 8.1","LS106 L NIVO B130 "," ----SPARE------- ","L8-83","2\\3\\5",null,"395\\3",null,"A 15.0"]
["E 8.2","LS114 L NIVO B134 "," ----SPARE------- ","L8-84","2\\3\\6",null,"395\\4",null,"A 15.1"]
["E 8.3","LS117 L NIVO B135 "," ----SPARE------- ","L8-85","2\\3\\7",null,"395\\5",null,"A 15.2"]
["E 8.4","LS807 H NIVO B804","xxxxxxxxxxxxxxxx ","L8-86","2\\3\\8",null,"395\\6",null,"A 15.3"]
["E 8.5","LS100 H NIVO B128 ","UITVOERKLEP XEV-162.3 DOEKENFILTER OPEN","L8-87","2\\3\\9",null,"395\\7",null,"A 15.4"]
["E 8.6","LS108 H NIVO B132","xxxxxxxxxxxxxxxx ","L8-88","2\\3\\10",null,"395\\8",null,"A 15.5"]
["E 8.7","LS109 L NIVO B132","xxxxxxxxxxxxxxxx ","L8-89","2\\3\\11",null,"395\\9",null,"A 16.0"]
[";",";",";","L8-90","2\\3\\12",null,"395\\10",null,"A 16.1"]
["E 9.0","LS111 H NIVO B133","xxxxxxxxxxxxxxxx ","L8-91","2\\3\\13",null,"395\\11",null,"A 16.2"]
["E 9.1","LS119 H NIVO B137","xxxxxxxxxxxxxxxx ","L8-92","2\\3\\14",null,"395\\12",null,"A 16.3"]
["E 9.2","LS120 L NIVO B137","xxxxxxxxxxxxxxxx ","L8-93","2\\3\\15",null,"395\\13",null,"A 16.4"]
["E 9.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-94","2\\3\\16",null,"395\\14",null,"A 16.5"]
["E 9.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-95","2\\3\\17",null,"395\\15",null,"A 16.6"]
["E 9.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-96","2\\3\\18",null,"395\\16",null,"A 16.7"]
["E 9.6","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-97","2\\3\\19",null,"395\\17",null,"A 17.0"]
["E 9.7","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-98","2\\3\\20",null,"395\\18",null,"A 17.1"]
[";",";",";","L8-99","2\\3\\21","GND","395\\19",null,"A 17.2"]
[";",";",";","L8-100","2\\3\\22",null,"395\\20",null,"A 17.3"]
[";",";",";","L8-101","2\\3\\23",null,"395\\21",null,"A 17.4"]
[";",";",";","L8-102","2\\3\\24",null,"395\\22",null,"A 17.5"]
["E 10.0","ALARM AFZUIGING OVEN ","ALARM AFZUIGING OVEN ","L8-103","2\\3\\25",null,"395\\23",null,"A 17.6"]
["E 10.1","HOOG NIVO STOFVAT AFZ.OVEN ","HOOG NIVO STOFVAT AFZ.OVEN ","L8-104","2\\3\\26",null,"395\\24",null,"A 17.7"]
["E 10.2","ALARM AFZUIGING HANDLING ","ALARM AFZUIGING HANDLING ","L8-105","2\\3\\27",null,"395\\25",null,"A 18.0"]
["E 10.3","HOOG NIVO STOFVAT AFZ.HANDLING ","HOOG NIVO STOFVAT AFZ.HANDLING ","L8-106","2\\3\\28",null,"395\\26",null,"A 18.1"]
["E 10.4","MA162 CONTACTOR FEEDBACK","MA162 CONTACTOR FEEDBACK","L8-107","2\\3\\29",null,"395\\27",null,"A 18.2"]
["E 10.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-108","2\\3\\30",null,"395\\28",null,"A 18.3"]
["E 10.6","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-109","2\\3\\31",null,"395\\29",null,"A 18.4"]
["E 10.7","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-110","2\\3\\32",null,"395\\30",null,"A 18.5"]
[";",";",";","L8-111","2\\3\\33",null,"395\\31",null,"A 18.6"]
["E 11.0"," ----SPARE------- "," ----SPARE------- ","L8-112","2\\3\\34",null,"395\\32",null,"A 18.7"]
["E 11.1","TZS176O LUCHT KLEP S150 OPEN ","TZS176O LUCHT KLEP S150 OPEN ","L8-113","2\\3\\35",null,"395\\33",null,"A 19.0"]
["E 11.2","TZS176C LUCHT KLEP S150 DICHT ","TZS176C LUCHT KLEP S150 DICHT ","L8-114","2\\3\\36",null,"395\\34",null,"A 19.1"]
["E 11.3"," ----SPARE------- "," ----SPARE------- ","L8-115","2\\3\\37",null,"395\\35",null,"A 19.2"]
["E 11.4"," ----SPARE------- "," ----SPARE------- ","L8-116","2\\3\\38",null,"395\\36",null,"A 19.4"]
["E 11.5","MGSO4-SP SPANNING AANWEZIG (VACUUMFILTER ","SPANNING AANWEZIG                            MGSO4","L8-117","2\\3\\39",null,"395\\37","pag.0013","A 19.5"]
["E 11.6","XZS150-2 XPV150 DICHT ","UITVOERKLEP XEV-162.1 DOEKENFILTER OPEN","L8-118","2\\3\\40",null,"395\\38",null,"A 19.6"]
["E 11.7","XZS150-1 XPV150 OPEN ","UITVOERKLEP XEV-162.1 DOEKENFILTER DICHT","L8-119","2\\3\\41",null,"395\\39",null,"A 19.7"]
[";",";",";","L8-120","2\\3\\42",null,"395\\PE",null,"AW 0"]
[";",";",";","L8-121","2\\4\\3","24VDC","396\\1",null,"E 0.0"]
["E 12.0","MA150 CONTACTOR FEEDBACK (K9816)","MA150 CONTACTOR FEEDBACK ","L8-122","2\\4\\4",null,"396\\2","S-150","E 0.2"]
["E 12.1","MA151 CONTACTOR FEEDBACK (K9902)","MA151 CONTACTOR FEEDBACK ","L8-123","2\\4\\5",null,"396\\3","S-151","E 0.4"]
["E 12.2"," ----SPARE------- "," ----SPARE------- ","L8-124","2\\4\\6",null,"396\\4",null,"E 0.5"]
["E 12.3"," ----SPARE------- "," ----SPARE------- ","L8-125","2\\4\\7",null,"396\\5",null,"E 0.6"]
["E 12.4","XZS182 STANDMELDING XEV182 OMLOOP P150 "," ----SPARE------- ","L8-126","2\\4\\8",null,"396\\6",null,"E 1.0"]
["E 12.5","MA182 CONTACTOR FEEDBACK","MA156 CONTACTOR FEEDBACK ","L8-127","2\\4\\9",null,"396\\7",null,"E 1.1"]
["E 12.6","MA158 CONTACTOR FEEDBACK ","MA152 CONTACTOR FEEDBACK ","L8-128","2\\4\\10",null,"396\\8",null,"E 1.2"]
["E 12.7","K9616","MA160.3 CONTACTOR FEEDBACK ","L8-129","2\\4\\11",null,"396\\9",null,"E 1.3"]
[";",";",";","L8-130","2\\4\\12",null,"396\\10",null,"E 1.4"]
["E 13.0","MA160-1 CONTACTOR FEEDBACK ","MA160-1 CONTACTOR FEEDBACK ","L8-131 ","2\\4\\13",null,"396\\11",null,"E 1.6"]
["E 13.1"," ----SPARE------- "," ----SPARE------- ","L8-132","2\\4\\14",null,"396\\12",null,"E 1.7"]
["E 13.2","MA179 CONTACTOR FEEDBACK ","MA179 CONTACTOR FEEDBACK ","L8-133","2\\4\\15",null,"396\\13",null,"E 2.0"]
["E 13.3","MA160-2 CONTACTOR FEEDBACK ","MA160-2 CONTACTOR FEEDBACK ","L8-134","2\\4\\16",null,"396\\14",null,"E 2.1"]
["E 13.4","XA901 TRAFO IN STORING ","XA901 TRAFO IN STORING ","L8-135","2\\4\\17",null,"396\\15",null,"E 2.2"]
["E 13.5","MA168 CONTACTOR FEEDBACK","MA153 CONTACTOR FEEDBACK ","L8-136","2\\4\\18",null,"396\\16",null,"E 2.3"]
["E 13.6","MK150 CONTACTOR FEEDBACK ","MK150 CONTACTOR FEEDBACK ","L8-137","2\\4\\19",null,"396\\17",null,"E 2.4"]
["E 13.7","MK151.1 CONTACTOR FEEDBACK ","MK151.1 CONTACTOR FEEDBACK ","L8-138","2\\4\\20",null,"396\\18",null,"E 2.6"]
[";",";",";","L8-139","2\\4\\21","GND","396\\19",null,"E 2.7"]
[";",";",";","L8-140","2\\4\\22",null,"396\\20",null,"E 3.1"]
[";",";",";","L8-141","2\\4\\23",null,"396\\21",null,"E 3.2"]
[";",";",";","L8-142","2\\4\\24",null,"396\\22",null,"E 3.3"]
["E 14.0","MK152 CONTACTOR FEEDBACK ","MK152 CONTACTOR FEEDBACK ","L8-143","2\\4\\25",null,"357\\23",null,"E 3.4"]
["E 14.1","MA173 CONTACTOR FEEDBACK ","MP804 CONTACTOR FEEDBACK ","L8-144","2\\4\\26",null,"396\\24",null,"E 3.5"]
["E 14.2","MA156 CONTACTOR FEEDBACK ","MA152.1 CONTACTOR FEEDBACK ","L8-145","2\\4\\27",null,"396\\25",null,"E 3.6"]
["E 14.3","MA178 CONTACTOR FEEDBACK "," ----SPARE------- ","L8-146","2\\4\\28",null,"396\\26",null,"E 3.7"]
["E 14.4","MA157 CONTACTOR FEEDBACK ","XEV157 CONTACTOR FEEDBACK ","L8-147","2\\4\\29",null,"396\\27",null,"E 4.0"]
["E 14.5","MK158 CONTACTOR FEEDBACK ","MK910 CONTACTOR FEEDBACK ","L8-148","2\\4\\30",null,"396\\28",null,"E 4.2"]
["E 14.6","K9904","MK151.2 CONTACTOR FEEDBACK ","L8-149","2\\4\\31",null,"396\\29","MP150-1","E 4.3"]
["E 14.7","MP151 CONTACTOR FEEDBACK","MP815.2 CONTACTOR FEEDBACK ","L8-150","2\\4\\32",null,"336\\30",null,"E 4.4"]
[";",";",";","L8-151","2\\4\\33",null,"396\\31",null,"E 4.5"]
["E 15.0","F818-2(24VDC) - L7\\85 - 5K6A SALDEN KAST PLC","MK818.2 CONTACTOR FEEDBACK ","L8-152","2\\4\\34",null,"396\\32","MK818-2","E 4.6"]
["E 15.1","MS159 CONTACTOR FEEDBACK"," ----SPARE------- ","L8-153","2\\4\\35",null,"396\\33",null,"E 4.7"]
["E 15.2"," ----SPARE------- "," ----SPARE------- ","L8-154","2\\4\\36",null,"396\\34",null,"E 5.0"]
["E 15.3"," ----SPARE------- "," ----SPARE------- ","L8-155","2\\4\\37",null,"396\\35",null,"E 5.1"]
["E 15.4"," ----SPARE------- "," ----SPARE------- ","L8-156","2\\4\\38",null,"396\\36",null,"E 5.3"]
["E 15.5","FS199 VERBR.LUCHT FLOW < MIN ","FS199 VERBR.LUCHT FLOW < MIN ","L8-157","2\\4\\39",null,"396\\37",null,"E 5.4"]
["E 15.6"," ----SPARE------- "," ----SPARE------- ","L8-158","2\\4\\40",null,"396\\38",null,"E 5.5"]
["E 15.7","MA156.1 CONTACTOR FEEDBACK ","MA156.1 CONTACTOR FEEDBACK ","L8-159","2\\4\\41",null,"396\\39",null,"E 5.6"]
[";",";",";","L8-160","2\\4\\42",null,"396\\PE",null,"E 5.7"]
[";",";",";","L8-161","2\\5\\3","24VDC","397\\1",null,"E 6.7"]
["E 16.0","MP832 MOTOR LOOPT (VACUUMFILTER) ","STORING FREQ REG.                              MGSO4","L8-162","2\\5\\4",null,"397\\2","pag.0014","E 7.0"]
["E 16.1","XS832 KLEPSTAND (VACUUMFILTER) ","ROERWERK TANK 1 STORING                 MGSO4","L8-163","2\\5\\5",null,"397\\3","pag.0014","E 7.1"]
["E 16.2","RTO NOODVOEDING STORING/STAND-BY (0/1)","RTO NOODVOEDING STORING/STAND-BY (0/1)","L8-164","2\\5\\6",null,"397\\4",null,"E 7.2"]
["E 16.3","RTO NETVOEDING NIET/WEL AANWEZIG (0/1) ","RTO NETVOEDING NIET/WEL AANWEZIG (0/1) ","L8-165","2\\5\\7",null,"397\\5",null,"E 7.3"]
["E 16.4","TS157-2 OVERLOAD ERROR P156-1 (SEAC) ","TS157-2 OVERLOAD ERROR P156-1        (SEAC) ","L8-166","2\\5\\8",null,"397\\6",null,"E 7.4"]
["E 16.5","FS156-1 P156-1 FLOW (SEAC) ","FS156-1 P156-1 FLOW                             (SEAC) ","L8-167","2\\5\\9",null,"397\\7",null,"E 7.6"]
["E 16.6","XS154 WATER P156-1 RUN NO FLOW (SEAC) ","XS154 WATER P156-1 RUN NO FLOW      (SEAC) ","L8-168","2\\5\\10",null,"397\\8",null,"E 7.7"]
["E 16.7","XS153 WATER P156-2 RUN NO FLOW (SEAC) ","XS153 WATER P156-2 RUN NO FLOW      (SEAC) ","L8-169","2\\5\\11",null,"397\\9",null,"E 8.5"]
[";",";",";","L8-170","2\\5\\12",null,"397\\10",null,"E 8.6"]
["E 17.0","MP156-2 MOTOR LOOPT (SEAC) ","MP156-2 MOTOR LOOPT                          (SEAC) ","L8-171","2\\5\\13",null,"397\\11",null,"E 10.4"]
["E 17.1"," ----SPARE------- "," ----SPARE------- ","L8-172","2\\5\\14",null,"397\\12",null,"E 11.5"]
["E 17.2"," ----SPARE------- "," ----SPARE------- ","L8-173","2\\5\\15",null,"397\\13",null,"E 11.6"]
["E 17.3"," ----SPARE------- "," ----SPARE------- ","L8-174","2\\5\\16",null,"397\\14",null,"E 11.7"]
["E 17.4"," ----SPARE------- "," ----SPARE------- ","L8-175","2\\5\\17",null,"397\\15",null,"E 12.0"]
["E 17.5","TS157-1 OVERLOAD ERROR P156-2 (SEAC) ","TS157-1 OVERLOAD ERROR P156-2        (SEAC) ","L8-176","2\\5\\18",null,"397\\16",null,"E 12.1"]
["E 17.6","FS156-2 P156-2 FLOW (SEAC) ","FS156-2 P156-2 FLOW                             (SEAC) ","L8-177","2\\5\\19",null,"397\\17",null,"E 12.2"]
["E 17.7"," ----SPARE------- "," ----SPARE------- ","L8-178","2\\5\\20",null,"397\\18",null,"E 12.3"]
[";",";",";","L8-179","2\\5\\21","GND","397\\19",null,"E 12.4"]
[";",";",";","L8-180","2\\5\\22",null,"397\\20",null,"E 12.5"]
[";",";",";","L8-181","2\\5\\23",null,"397\\21",null,"E 12.6"]
[";",";",";","L8-182","2\\5\\24",null,"397\\22",null,"E 12.7"]
["E 18.0","ZS150 ERROR MODE (SEAC) ","ZS150 ERROR MODE                              (SEAC) ","L8-183","2\\5\\25",null,"397\\23",null,"E 13.0"]
["E 18.1","ES150 GEREED VOOR BESTURING (SEAC) ","ES150 GEREED VOOR BESTURING        (SEAC) ","L8-184","2\\5\\26",null,"397\\24",null,"E 13.1"]
["E 18.2","ES152 24VAC AANWEZIG (SEAC) ","ES152 24VAC AANWEZIG                       (SEAC) ","L8-185","2\\5\\27",null,"397\\25",null,"E 13.2"]
["E 18.3","ES151 24VDC AANWEZIG (SEAC) ","ES151 24VDC AANWEZIG                       (SEAC) ","L8-186","2\\5\\28",null,"397\\26",null,"E 13.3"]
["E 18.4","TS156 WATER TEMP. P156-1/P156-2 (SEAC) ","TS156 WATER TEMP. P156-1/P156-2       (SEAC) ","L8-187","2\\5\\29",null,"397\\27",null,"E 13.4"]
["E 18.5","PS156 SEAC UITLAAT DRUK ","PS156 SEAC UITLAAT DRUK ","L8-188","2\\5\\30",null,"397\\28",null,"E 13.5"]
["E 18.6","ES153 VOEDING 3~ OK (SEAC) ","ES153 VOEDING 3~ OK                          (SEAC) ","L8-189","2\\5\\31",null,"397\\29",null,"E 13.6"]
["E 18.7","LS171-1 L NIVO V156 ","LS171-1 L NIVO V156","L8-190","2\\5\\32",null,"397\\30",null,"E 13.7"]
[";",";",";","L8-191","2\\5\\33",null,"397\\31",null,"E 14.0"]
["E 19.0","LS171-2 H NIVO V156 ","LS171-2 H NIVO V156","L8-192","2\\5\\34",null,"397\\32",null,"E 14.1"]
["E 19.1","XS152 WATER LEVEL TR. OFF (SEAC) ","XS152 WATER LEVEL TR. OFF                (SEAC) ","L8-193","2\\5\\35",null,"397\\33",null,"E 14.2"]
["E 19.2","PS199 L DRUK SPOELLUCHT ","PS199 L DRUK SPOELLUCHT ","L8-194","2\\5\\36",null,"397\\34",null,"E 14.3"]
["E 19.3"," ----SPARE------- "," ----SPARE------- ","L8-195","2\\5\\37",null,"397\\35",null,"E 14.4"]
["E 19.4","XS113-1 XEV113 TOEVOER WATER (SEAC) ","XS113-1 XEV113 TOEVOER WATER         (SEAC) ","L8-196","2\\5\\38",null,"397\\36",null,"E 14.5"]
["E 19.5"," ----SPARE------- "," ----SPARE------- ","L8-197","2\\5\\39",null,"397\\37",null,"E 14.6"]
["E 19.6","XS112-1 XEV112 TOEVOER LUCHT (SEAC) ","XS112-1 XEV112 TOEVOER LUCHT           (SEAC) ","L8-198","2\\5\\40",null,"397\\38",null,"E 14.7"]
["E 19.7","PS129 L DRUK WATER INL.KLEPSTATION (SEAC ","PS129 L DRUK WATER INL.KLEPSTATION (SEAC ","L8-199","2\\5\\41",null,"397\\39",null,"E 15.0"]
[";",";",";","L8-200","2\\5\\42",null,"397\\PE",null,"E 15.1"]
[";",";",";","L8-201","2\\6\\3","24VDC","398\\1",null,"E 15.7"]
["E 20.0 ","PS115 L DRUK LUCHT INL.KLEPSTATION (SEAC ","PS115 L DRUK LUCHT INL.KLEPSTATION (SEAC ","L8-202","2\\6\\4",null,"398\\2",null,"E 16.0"]
["E 20.1","PS118 L DRUK LUCHT UITL.KLEPSTATION (SEA ","PS118 L DRUK LUCHT UITL.KLEPSTATION (SEA ","L8-203","2\\6\\5",null,"398\\3",null,"E 16.1"]
["E 20.2","XS113 XPV EINDSTAND WATER (SEAC) ","XS113 XPV EINDSTAND WATER             (SEAC) ","L8-204","2\\6\\6",null,"398\\4",null,"E 16.2"]
["E 20.3"," ----SPARE------- "," ----SPARE------- ","L8-205","2\\6\\7",null,"398\\5",null,"E 16.3"]
["E 20.4"," ----SPARE------- "," ----SPARE------- ","L8-206","2\\6\\8",null,"398\\6",null,"E 16.4"]
["E 20.5"," ----SPARE------- "," ----SPARE------- ","L8-207","2\\6\\9",null,"398\\7",null,"E 16.5"]
["E 20.6","TSH165-2 TEMPERATUUR BOVEN IN KETEL ","TSH165-2 TEMPERATUUR BOVEN IN KETEL ","L8-208","2\\6\\10",null,"398\\8",null,"E 16.6"]
["E 20.7"," ----SPARE------- "," ----SPARE------- ","L8-209","2\\6\\11",null,"398\\9",null,"E 16.7"]
[";",";",";","L8-210","2\\6\\12",null,"398\\10",null,"E 17.0"]
["E 21.0 "," ----SPARE------- "," ----SPARE------- ","L8-211","2\\6\\13",null,"398\\11",null,"E 17.3"]
["E 21.1","XEV833 KLEP STATUS (VACUUMFILTER) ",null,"L8-212","2\\6\\14",null,"398\\12",null,"E 17.4"]
["E 21.2"," ----SPARE------- "," ----SPARE------- ","L8-213","2\\6\\15",null,"398\\13",null,"E 17.5"]
["E 21.3","XS112 XPV EINDSTAND LUCHT (SEAC) ","XS112 XPV EINDSTAND LUCHT                (SEAC) ","L8-214","2\\6\\16",null,"398\\14",null,"E 17.6"]
["E 21.4","XS114 WATER INJECTIE GESTART (SEAC) ","XS114 WATER INJECTIE GESTART          (SEAC) ","L8-215","2\\6\\17",null,"398\\15",null,"E 18.0"]
["E 21.5","LS171-1 LL NIVO V156 ","LS171-1 LL NIVO V156","L8-216","2\\6\\18",null,"398\\16",null,"E 18.1"]
["E 21.6","TS171-1 L TEMP ROOKGAS INL.C150 (SEAC) ","TS171-1 L TEMP ROOKGAS INL.C150      (SEAC) ","L8-217","2\\6\\19",null,"398\\17",null,"E 18.2"]
["E 21.7","TS171-2 H TEMP ROOKGAS INL.C150 (SEAC) ","TS171-2 H TEMP ROOKGAS INL.C150      (SEAC) ","L8-218","2\\6\\20",null,"398\\18",null,"E 18.3"]
[";",";",";","L8-219","2\\6\\21","GND","398\\19",null,"E 18.4"]
[";",";",";","L8-220","2\\6\\22",null,"398\\20",null,"E 18.5"]
[";",";",";","L8-221","2\\6\\23",null,"398\\21",null,"E 18.6"]
[";",";",";","L8-222","2\\6\\24",null,"398\\22",null,"E 18.7"]
["E 22.0","MP833 MOTOR LOOPT (VACUUMFILTER)","ROERWERK T2 STORING                         MGSO4","L8-223","2\\6\\25",null,"398\\23","pag.0014","E 19.0"]
["E 22.1","XS833 KLEPSTAND (VACUUMFILTER) ","STORING KOELM.FREQ.REG.                  MGSO4","L8-224","2\\6\\26",null,"398\\24","pag.0014","E 19.1"]
["E 22.2","MP831 MOTOR LOOPT (VACUUMFILTER) ","HOOG=T1 RETOUR LAAG = T2 RETOUR   MGSO4","L8-225","2\\6\\27",null,"398\\25","pag.0014","E 19.2"]
["E 22.3","MP830 MOTOR LOOPT (VACUUMFILTER) ","HOOG=T1 LEGEN LAAG = T2 LEGEN       MGSO4","L8-226","2\\6\\28",null,"398\\26","pag.0015","E 19.3"]
["E 22.4","XS912 KLEPSTAND (VACUUMFILTER) ","HOOG NIVO TANK1                                  MGSO4","L8-227","2\\6\\29",null,"398\\27","pag.0015","E 19.4"]
["E 22.5","XS805-1 KLEPSTAND (VACUUMFILTER) ","LAAG NIVO TANK 1                                  MGSO4","L8-228","2\\6\\30",null,"398\\28","pag.0015","E 19.5"]
["E 22.6","XS805-2 KLEPSTAND (VACUUMFILTER) ","VOORALARM LAAG NIVO TANK 1            MGSO4","L8-229","2\\6\\31",null,"398\\29","pag.0015","E 19.6"]
["E 22.7","XS830-2 KLEPSTAND (VACUUMFILTER) ","HOOG NIVO TANK 2                                 MGSO4","L8-230","2\\6\\32",null,"398\\30",null,"E 19.7"]
[";",";",";","L8-231","2\\6\\33",null,"398\\31",null,"E 20.0"]
["E 23.0","XS830-1 KLEPSTAND (VACUUMFILTER) ","LAAG NIVO TANK 2                                  MGSO4","L8-232","2\\6\\34",null,"398\\32","pag.0016","E 20.1"]
["E 23.1","XA.. THERMISCHE STORING (VACUUMFILTER) ","VOORALARM LAAG NIVO TANK 2            MGSO4","L8-233","2\\6\\35",null,"398\\33","pag.0016","E 20.2"]
["E 23.2"," ----SPARE------- "," ----SPARE------- ","L8-234","2\\6\\36",null,"398\\34",null,"E 20.3"]
["E 23.3"," ----SPARE------- "," ----SPARE------- ","L8-235","2\\6\\37",null,"398\\35",null,"E 20.4"]
["E 23.4","SEAC BESTURING STAND-BY ","SEAC BESTURING STAND-BY ","L8-236","2\\6\\38",null,"398\\36",null,"E 20.5"]
["E 23.5"," ----SPARE------- "," ----SPARE------- ","L8-237","2\\6\\39",null,"398\\37",null,"E 20.6"]
["E 23.6"," ----SPARE------- "," ----SPARE------- ","L8-238","2\\6\\40",null,"398\\38",null,"E 20.7"]
["E 23.7"," ----SPARE------- "," ----SPARE------- ","L8-239","2\\6\\41",null,"398\\39",null,"E 21.0"]
[";",";",";","L8-240","2\\6\\42",null,"398\\PE",null,"E 21.1"]
[";",";",";","L8-241","2\\7\\3","24VDC","399\\1",null,"E 21.2"]
["E 24.0","FS815-1 TOEVOER SPROEIERS C815 LAAG ","FS815-1 TOEVOER SPROEIERS C815 LAAG ","L8-242","2\\7\\4",null,"399\\2",null,"E 21.3"]
["E 24.1","FS815-2 TOEVOER INL. SPROEIERS C815 LAAG ","FS815-2 TOEVOER INL. SPROEIERS C815 LAAG ","L8-243","2\\7\\5",null,"399\\3",null,"E 21.4"]
["E 24.2","LS800-2 LL NIVO V800A ","LS800-2 LL NIVO V800A ","L8-244","2\\7\\6",null,"399\\4",null,"E 21.5"]
["E 24.3","LS800-3 HH NIVO V800A ","LS800-3 HH NIVO V800A ","L8-245","2\\7\\7",null,"399\\5",null,"E 21.6"]
["E 24.4","LS800-5 LL NIVO V800B ","LS800-5 LL NIVO V800B ","L8-246","2\\7\\8",null,"399\\6",null,"E 21.7"]
["E 24.5","LS800-7 HH NIVO TANKAUTO ","LS800-7 HH NIVO V-200 ","L8-247","2\\7\\9",null,"399\\7",null,"E 22.0"]
["E 24.6","LS802-2 LL NIVO V802 ","LS802-2 LL NIVO V802","L8-248","2\\7\\10",null,"399\\8",null,"E 22.1"]
["E 24.7","LS804-2 LL NIVO V804 ","LS804-2 LL NIVO V804","L8-249","2\\7\\11",null,"399\\9",null,"E 22.2"]
[";",";",";","L8-250","2\\7\\12",null,"399\\10",null,"E 22.3"]
["E 25.0","LS804-3 HH NIVO V804 ","LS804-3 HH NIVO V804","L8-251","2\\7\\13",null,"399\\11",null,"E 22.4"]
["E 25.1","LS816 H NIVO C816 ","LS816 H NIVO C816 ","L8-252","2\\7\\14",null,"399\\12",null,"E 22.5"]
["E 25.2","LS817 H NIVO C817 ","LS817 H NIVO C817 ","L8-253","2\\7\\15",null,"399\\13",null,"E 22.6"]
["E 25.3","LS818 H NIVO C818 ","LS818 H NIVO C818 ","L8-254","2\\7\\16",null,"399\\14",null,"E 22.7"]
["E 25.4","LS819-2 LL NIVO V819 ","LS819-2 LL NIVO V170","L8-255","2\\7\\17","F819.2","399\\15","L819","E 23.0"]
["E 25.5","F820.2(24VDC) LS820-2 LL NIVO V820 ","LS820-2 LL NIVO V820 ","L8-256","2\\7\\18",null,"399\\16","L820","E 23.1"]
["E 25.6","F820.3(24VDC) LS820-3 LL NIVO V820 ","LS820-3 LL NIVO V820 ","L8-257","2\\7\\19",null,"399\\17","L820","E 23.4"]
["E 25.7","MP800 CONTACTOR FEEDBACK ","MP800 CONTACTOR FEEDBACK ","L8-258","2\\7\\20",null,"399\\18",null,"E 24.1"]
[";",";",";","L8-259","2\\7\\21","GND","399\\19",null,"E 24.2"]
[";",";",";","L8-260","2\\7\\22",null,"399\\20",null,"E 24.3"]
[";",";",";","L8-261","2\\7\\23",null,"399\\21",null,"E 24.4"]
[";",";",";","L8-262","2\\7\\24",null,"399\\22",null,"E 24.5"]
["E 26.0","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-263","2\\7\\25",null,"399\\23",null,"E 24.6"]
["E 26.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-264","2\\7\\26",null,"399\\24",null,"E 24.7"]
["E 26.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-265","2\\7\\27",null,"399\\25",null,"E 25.0"]
["E 26.3","MP802A CONTACTOR FEEDBACK ","MP802A CONTACTOR FEEDBACK ","L8-266","2\\7\\28",null,"399\\26",null,"E 25.1"]
["E 26.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-267","2\\7\\29",null,"399\\27",null,"E 25.2"]
["E 26.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-268","2\\7\\30",null,"399\\28",null,"E 25.3"]
["E 26.6","MA161 CONTACTOR FEEDBACK ","MA161 CONTACTOR FEEDBACK ","L8-269","2\\7\\31",null,"399\\29",null,"E 25.5"]
["E 26.7","MM802 CONTACTOR FEEDBACK ","MM802 CONTACTOR FEEDBACK ","L8-270","2\\7\\32",null,"399\\30",null,"E 25.6"]
[";",";",";","L8-271","2\\7\\33",null,"399\\31",null,"E 25.7"]
["E 27.0","MK151.2 VIBRO HOOG ","MK151.2 VIBRO HOOG ","L8-272","2\\7\\34",null,"399\\32",null,"E 26.3"]
["E 27.1","MK151.2 VIBRO HOOGHOOG ","MK151.2 VIBRO HOOGHOOG ","L8-273","2\\7\\35",null,"399\\33",null,"E 26.6"]
["E 27.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-274","2\\7\\36",null,"399\\34",null,"E 26.7"]
["E 27.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-275","2\\7\\37",null,"399\\35",null,"E 27.6"]
["E 27.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-276","2\\7\\38",null,"399\\36",null,"E 27.7"]
["E 27.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-277","2\\7\\39",null,"399\\37",null,"E 28.0"]
["E 27.6","MP804 CONTACTOR FEEDBACK","MA151.1 CONTACTOR FEEDBACK ","L8-278","2\\7\\40",null,"399\\38",null,"E 28.1"]
["E 27.7","MM804 CONTACTOR FEEDBACK","MM804 CONTACTOR FEEDBACK","L8-279","2\\7\\41",null,"399\\39",null,"E 28.2"]
[";",";",";","L8-280","2\\7\\42",null,"399\\PE",null,"E 28.7"]
[";",";",";","L8-281","2\\8\\3","24VDC","400\\1",null,"E 29.0"]
["E 28.0","MP805 CONTACTOR FEEDBACK ","MP805 CONTACTOR FEEDBACK ","L8-282","2\\8\\4",null,"400\\2",null,"E 29.1"]
["E 28.1","MP815.1 CONTACTOR FEEDBACK ","MP815.1 CONTACTOR FEEDBACK ","L8-283","2\\8\\5",null,"400\\3",null,"E 29.4"]
["E 28.2","MK820B CONTACTOR FEEDBACK ","MK820B CONTACTOR FEEDBACK ","L8-284","2\\8\\6",null,"400\\4",null,"E 29.5"]
["E 28.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-285","2\\8\\7",null,"400\\5",null,"E 29.6"]
["E 28.4","MK151.X TRACING FEEDBACK ","ZUIGLEIDING MK-151.1 EN 2 TRACING FEEDBACK ","L8-286","2\\8\\8",null,"400\\6",null,"E 30.0"]
["E 28.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-287","2\\8\\9",null,"400\\7",null,"E 30.1"]
["E 28.6","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-288","2\\8\\10",null,"400\\8",null,"E 30.4"]
["E 28.7","MP816A CONTACTOR FEEDBACK ","MP816A CONTACTOR FEEDBACK ","L8-289","2\\8\\11",null,"400\\9",null,"E 31.2"]
[";",";",";","L8-290","2\\8\\12",null,"400\\10",null,"E 31.5"]
["E 29.0","TS155-1 BUITENLUCHT TEMP < 1 GRD.C ","TS155-1 BUITENLUCHT TEMP < 1 GRD.C ","L8-291","2\\8\\13",null,"400\\11",null,"E 31.6"]
["E 29.1","TS155-2 BUITENLUCHT TEMP < -5 GRD.C ","TS155-2 BUITENLUCHT TEMP < -5 GRD.C ","L8-292","2\\8\\14",null,"400\\12",null,"E 31.7"]
["E 29.2","LS161 L NIVO MOBREY HOOFDDRUM ","NIVO ALARMERING CONUS DOEKENFILTER 2","L8-293","2\\8\\15",null,"400\\13",null,"E 32.0"]
["E 29.3","LS162 L NIVO MOBREY NEVENDRUM ","NIVO ALARMERING CONUS DOEKENFILTER 3","L8-294","2\\8\\16",null,"400\\14",null,"E 32.1"]
["E 29.4","MS816A-1 START KNOP MP816A ","MS816A-1 START KNOP MP816A ","L8-295","2\\8\\17",null,"400\\15",null,"E 32.2"]
["E 29.5","MS816B-1 STOP KNOP MP816A ","MS816B-1 STOP KNOP MP816A ","L8-296","2\\8\\18",null,"400\\16",null,"E 32.5"]
["E 29.6","FS156 KOELWATER CONDENSAAT P151 "," ----SPARE------- ","L8-297","2\\8\\19",null,"400\\17",null,"E 32.6"]
["E 29.7","FS165 KOELWATER SCHROEF A158 ","WORDT DE TRILTOREN OOIT","L8-298","2\\8\\20",null,"400\\18",null,"E 33.0"]
[";",";",";","L8-299","2\\8\\21","GND","400\\19",null,"E 33.6"]
[";",";",";","L8-300","2\\8\\22",null,"400\\20",null,"E 33.7"]
[";",";",";","L8-301","2\\8\\23",null,"400\\21",null,"E 34.3"]
[";",";",";","L8-302","2\\8\\24",null,"400\\22",null,"E 34.4"]
["E 30.0","MP816B CONTACTOR FEEDBACK ","MP816B CONTACTOR FEEDBACK ","L8-303","2\\8\\25",null,"400\\23",null,"E 34.7"]
["E 30.1","MS816A-2 START KNOP MP816B ","MS816A-2 START KNOP MP816B ","L8-304","2\\8\\26",null,"400\\24",null,"E 35.7"]
["E 30.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-305","2\\8\\27",null,"400\\25",null,"E 36.3"]
["E 30.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-306","2\\8\\28",null,"400\\26",null,"E 36.4"]
["E 30.4","LS830-1 H NIVO V830 ",null,"L8-307","2\\8\\29",null,"400\\27",null,"E 36.5"]
["E 30.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-308","2\\8\\30",null,"400\\28",null,"E 36.6"]
["E 30.6","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-309","2\\8\\31",null,"400\\29",null,"E 36.7"]
["E 30.7","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-310","2\\8\\32",null,"400\\30",null,"E 37.0"]
[";",";",";","L8-311","2\\8\\33",null,"400\\31",null,"E 37.1"]
["E 31.0","MF830 MOTOR LOOPT (VACUUMFILTER) ","POMP IN BEDRIJF                                    MGSO4","L8-312","2\\8\\34",null,"400\\32","pag.0013","E 37.2"]
["E 31.1","XA.. NOODSTOP BEDIEND (VACUUMFILTER) ","NOODSTOP NIET BEDIEND                      MGSO4","L8-313","2\\8\\35",null,"400\\33","pag.0013","E 37.3"]
["E 31.2","HC1001 WERKSCHAKELAAR IN ","HC1001 WERKSCHAKELAAR IN ","L8-314","2\\8\\36",null,"400\\34",null,"E 37.4"]
["E 31.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-315","2\\8\\37",null,"400\\35",null,"E 37.5"]
["E 31.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-316","2\\8\\38",null,"400\\36",null,"E 37.6"]
["E 31.5","MP1001 GENERAL ALARM ","MP1001 GENERAL ALARM ","L8-317","2\\8\\39",null,"400\\37",null,"E 37.7"]
["E 31.6","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-318","2\\8\\40",null,"400\\38",null,"E 38.0"]
["E 31.7","XPV1008 KLEP OPEN "," ----SPARE------- ","L8-319","2\\8\\41",null,"400\\39",null,"E 38.1"]
[";",";",";","L8-320","2\\8\\42",null,"400\\PE",null,"E 38.2"]
[";",";",";","L8-321","2\\9\\3","24VDC","401\\1",null,"E 38.4"]
["E 32.0","XPV1008 KLEP DICHT "," ----SPARE------- ","L8-322","2\\9\\4",null,"401\\2",null,"E 38.5"]
["E 32.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-323","2\\9\\5",null,"401\\3",null,"E 38.6"]
["E 32.2","DRUK AARDGASTOEVOER >MIN.","BEVEIL.KOELVENT.PLC","L8-324","2\\9\\6",null,"401\\4",null,"E 38.7"]
["E 32.3","LA161 STORING MOBREY ","LA921NIVO ALARM CONUS DOEKENFILTER 2","L8-325","2\\9\\7",null,"401\\5",null,"E 39.0"]
["E 32.4","LA162 STORING MOBREY ","LA922NIVO ALARM CONUS DOEKENFILTER 3","L8-326","2\\9\\8",null,"401\\6",null,"E 39.1"]
["E 32.5","ES.. SLEUTEL OVERBR.INTERLOCKING BEDIEND ","ES.. SLEUTEL OVERBR.INTERLOCKING BEDIEND ","L8-327","2\\9\\9",null,"401\\7",null,"E 39.2"]
["E 32.6","PS167.1-L PS167-1 WERKLUCHTDRUK > 3,5 BAR ","PS167.1-L PS167-1 WERKLUCHTDRUK > 3,5 BAR ","L8-328","2\\9\\10",null,"401\\8",null,"E 39.3"]
["E 32.7","PS167.2-L PS167-2 WERKLUCHTDRUK > 1 BAR ","PS167.2-L PS167-2 WERKLUCHTDRUK > 1 BAR ","L8-329","2\\9\\11",null,"401\\9",null,"E 39.4"]
[";",";",";","L8-330","2\\9\\12",null,"401\\10",null,"E 39.5"]
["E 33.0","dPS169 H DRUK DOEKENFILTER F150 ","dPS169 H DRUK DOEKENFILTER F151","L8-331","2\\9\\13",null,"401\\11",null,"E 39.6"]
["E 33.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-332","2\\9\\14",null,"401\\12",null,"E 39.7"]
["E 33.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-333","2\\9\\15",null,"401\\13",null,"E 40.0"]
["E 33.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-334","2\\9\\16",null,"401\\14",null,"E 40.1"]
["E 33.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-335","2\\9\\17",null,"401\\15",null,"E 40.2"]
["E 33.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-336","2\\9\\18",null,"401\\16",null,"E 40.3"]
["E 33.6","XZS151-1 XPV151 OPEN ","UITVOERKLEP XEV162.2 DOEKENFILTER 2 OPEN","L8-337","2\\9\\19",null,"401\\17",null,"E 40.4"]
["E 33.7","XZS151-2 XPV151 DICHT ","UITVOERKLEP XEV162.2 DOEKENFILTER 2 DICHT","L8-338","2\\9\\20",null,"401\\18",null,"E 40.5"]
[";",";",";","L8-339","2\\9\\21","GND","401\\19",null,"E 40.6"]
[";",";",";","L8-340","2\\9\\22",null,"401\\20",null,"E 40.7"]
[";",";",";","L8-341","2\\9\\23",null,"401\\21",null,"E 41.0"]
[";",";",";","L8-342","2\\9\\24",null,"401\\22",null,"E 41.1"]
["E 34.0","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-343","2\\9\\25",null,"401\\23",null,"E 41.2"]
["E 34.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-344","2\\9\\26",null,"401\\24",null,"E 41.3"]
["E 34.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-345","2\\9\\27",null,"401\\25",null,"E 41.4"]
["E 34.3","FS155 KOELWATER CIRC. P150 "," ----SPARE------- ","L8-346","2\\9\\28",null,"401\\26",null,"E 41.5"]
["E 34.4","FS154 FLOW MINIMAAL "," ----SPARE------- ","L8-347","2\\9\\29",null,"401\\27",null,"E 41.6"]
["E 34.5","VUURHAARDDRUK < MAX. (PS-163)","xxxxxxxxxxxxxxxx ","L8-348","2\\9\\30",null,"401\\28",null,"E 41.7"]
["E 34.6","STOOMDRUK TE HOOG (PSH-151)","xxxxxxxxxxxxxxxx ","L8-349","2\\9\\31",null,"401\\29",null,"E 42.3"]
["E 34.7","MK172 CONTACTOR FEEDBACK ","MK172 CONTACTOR FEEDBACK ","L8-350","2\\9\\32",null,"401\\30",null,"E 43.0"]
[";",";",";","L8-351","2\\9\\33",null,"401\\31",null,"E 43.1"]
["E 35.0","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-352","2\\9\\34",null,"401\\32",null,"E 43.2"]
["E 35.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-353","2\\9\\35",null,"401\\33",null,"E 43.6"]
["E 35.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-354","2\\9\\36",null,"401\\34",null,"E 44.1"]
["E 35.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-355","2\\9\\37",null,"401\\35",null,"E 44.3"]
["E 35.4","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-356","2\\9\\38",null,"401\\36",null,"E 44.4"]
["E 35.5","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-357","2\\9\\39",null,"401\\37",null,"E 44.6"]
["E 35.6","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-358","2\\9\\40",null,"401\\38",null,"E 44.7"]
["E 35.7","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-359","2\\9\\41",null,"401\\39",null,"E 45.4"]
[";",";",";","L8-360","2\\9\\42",null,"401\\PE",null,"E 45.5"]
[";",";",";","L8-361","2\\10\\3","24VDC","402\\1",null,"E 46.0"]
["E 36.0","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-362","2\\10\\4",null,"402\\2",null,"E 46.2"]
["E 36.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-363","2\\10\\5",null,"402\\3",null,"E 47.0"]
["E 36.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-364","2\\10\\6",null,"402\\4",null,"E 47.2"]
["E 36.3","MK175 CONTACTOR FEEDBACK ","MK175 CONTACTOR FEEDBACK ","L8-365","2\\10\\7",null,"402\\5",null,"E 47.5"]
["E 36.4","MS816B-2 STOP KNOP MP816B ","MS816B-2 STOP KNOP MP816B ","L8-366","2\\10\\8",null,"402\\6",null,"E 48.0"]
["E 36.5","MP816C CONTACTOR FEEDBACK ","MP816C CONTACTOR FEEDBACK ","L8-367","2\\10\\9",null,"402\\7",null,"E 48.1"]
["E 36.6","MS816A-3 START KNOP MP816C ","MS816A-3 START KNOP MP816C ","L8-368","2\\10\\10",null,"402\\8",null,"E 48.3"]
["E 36.7","MS816B-3 STOP KNOP MP816C ","MS816B-3 STOP KNOP MP816C ","L8-369","2\\10\\11",null,"402\\9",null,"E 48.6"]
[";",";",";","L8-370","2\\10\\12",null,"402\\10",null,"E 49.0"]
["E 37.0 ","MK818.1 CONTACTOR FEEDBACK ","MK818.1 CONTACTOR FEEDBACK ","L8-371","2\\10\\13",null,"402\\11"]
["E 37.1","MP819 CONTACTOR FEEDBACK ","MP819 CONTACTOR FEEDBACK ","L8-372","2\\10\\14",null,"402\\12"]
["E 37.2","MK819 CONTACTOR FEEDBACK ","MK819 CONTACTOR FEEDBACK ","L8-373","2\\10\\15",null,"402\\13"]
["E 37.3","MK820A CONTACTOR FEEDBACK ","MK820A CONTACTOR FEEDBACK ","L8-374","2\\10\\16",null,"402\\14"]
["E 37.4","PS802 H DRUK HYDROXIDE P802A/S ","PS802 H DRUK HYDROXIDE P802A/S ","L8-375","2\\10\\17",null,"402\\15"]
["E 37.5","PS802 L DRUK HYDROXIDE P802A/S ","PS802 L DRUK HYDROXIDE P802A/S ","L8-376","2\\10\\18",null,"402\\16"]
["E 37.6","MP910A CONTACTOR FEEDBACK ","MP910A CONTACTOR FEEDBACK ","L8-377","2\\10\\19",null,"402\\17"]
["E 37.7","MP910S CONTACTOR FEEDBACK ","MP910S CONTACTOR FEEDBACK ","L8-378","2\\10\\20",null,"402\\18"]
[";",";",";","L8-379","2\\10\\21","GND","402\\19"]
[";",";",";","L8-380","2\\10\\22",null,"402\\20"]
[";",";",";","L8-381","2\\10\\23",null,"402\\21"]
[";",";",";","L8-382","2\\10\\24",null,"402\\22"]
["E 38.0"," ----SPARE------- "," ----SPARE------- ","L8-383","2\\10\\25",null,"402\\23"]
["E 38.1","dPS814-1 DEMISTER SCRUBBER C815 HOOG ","dPS814-1 DEMISTER SCRUBBER C815 HOOG ","L8-384","2\\10\\26",null,"402\\24"]
["E 38.2","dPS814-2 WARMTEWISSELAAR E815 HOOG ","dPS814-2 WARMTEWISSELAAR E815 HOOG ","L8-385","2\\10\\27",null,"402\\25"]
["E 38.3"," ----SPARE------- "," ----SPARE------- ","L8-386","2\\10\\28",null,"402\\26"]
["E 38.4","PS819-1 POST-OX. VENTILATOR K819 HOOG "," ----SPARE------- ","L8-387","2\\10\\29",null,"402\\27"]
["E 38.5","FS811-1 ROOKGAS TOEVOER C815 LAAG ","FS811-1 ROOKGAS TOEVOER C815 LAAG ","L8-388","2\\10\\30",null,"402\\28"]
["E 38.6"," ----SPARE------- "," ----SPARE------- ","L8-389","2\\10\\31",null,"402\\29"]
["E 38.7","TS811-1 L TEMP ROOKGAS TOEVOER ","TS811-1 L TEMP ROOKGAS TOEVOER ","L8-390","2\\10\\32",null,"402\\30"]
[";",";",";","L8-391","2\\10\\33",null,"402\\31"]
["E 39.0"," ----SPARE------- "," ----SPARE------- ","L8-392","2\\10\\34",null,"402\\32"]
["E 39.1"," ----SPARE------- "," ----SPARE------- ","L8-393","2\\10\\35",null,"402\\33"]
["E 39.2"," ----SPARE------- "," ----SPARE------- ","L8-394","2\\10\\36",null,"402\\34"]
["E 39.3","TS814-1 HH TEMP ROOKGAS UITL. KOELER","TS814-1 HH TEMP ROOKGAS UITL. KOELER","L8-395","2\\10\\37",null,"402\\35"]
["E 39.4"," ----SPARE------- "," ----SPARE------- ","L8-396","2\\10\\38",null,"402\\36"]
["E 39.5","XS812 VIBRATIE MK-818 HOOG ","XS812 VIBRATIE MK-818.1 HOOG ","L8-397","2\\10\\39",null,"402\\37"]
["E 39.6"," ----SPARE------- "," ----SPARE------- ","L8-398","2\\10\\40",null,"402\\38"]
["E 39.7"," ----SPARE-------"," ----SPARE-------","L8-399","2\\10\\41",null,"402\\39"]
[";",";",";","L8-400","2\\10\\42",null,"402\\PE"]
[";",";",";","L8-401","2\\11\\3","24VDC","403\\1"]
["E 40.0"," ----SPARE------- "," ----SPARE------- ","L8-402","2\\11\\4",null,"403\\2"]
["E 40.1","FS908 KOELWATER NAAR A173 ","FS908 KOELWATER NAAR TRILTOREN OOIT","L8-403","2\\11\\5",null,"403\\3"]
["E 40.2","FS911 KOELWATER NAAR Z815 ","FS911 KOELWATER NAAR Z816","L8-404","2\\11\\6",null,"403\\4"]
["E 40.3","FS912 KOELWATER NAAR E830 "," ----SPARE------- ","L8-405","2\\11\\7",null,"403\\5"]
["E 40.4","FS913 KOELWATER BESTAAND CIRCUIT ","FS913 KOELWATER BESTAAND CIRCUIT ","L8-406","2\\11\\8",null,"403\\6"]
["E 40.5"," ----SPARE------- "," ----SPARE------- ","L8-407","2\\11\\9",null,"403\\7"]
["E 40.6"," ----SPARE------- "," ----SPARE------- ","L8-408","2\\11\\10",null,"403\\8"]
["E 40.7"," ----SPARE------- "," ----SPARE------- ","L8-409","2\\11\\11",null,"403\\9"]
[";",";",";","L8-410","2\\11\\12",null,"403\\10"]
["E 41.0"," ----SPARE------- "," ----SPARE------- ","L8-411","2\\11\\13",null,"403\\11"]
["E 41.1"," ----SPARE------- "," ----SPARE------- ","L8-412","2\\11\\14",null,"403\\12"]
["E 41.2"," ----SPARE------- "," ----SPARE------- ","L8-413","2\\11\\15",null,"403\\13"]
["E 41.3","FS951 SEAL WATER LAAG ","FS951 SEAL WATER LAAG ","L8-414","2\\11\\16",null,"403\\14"]
["E 41.4"," ----SPARE------- "," ----SPARE------- ","L8-415","2\\11\\17",null,"403\\15"]
["E 41.5"," ----SPARE------- "," ----SPARE------- ","L8-416","2\\11\\18",null,"403\\16"]
["E 41.6"," ----SPARE------- "," ----SPARE------- ","L8-417","2\\11\\19",null,"403\\17"]
["E 41.7"," ----SPARE------- "," ----SPARE------- ","L8-418","2\\11\\20",null,"403\\18"]
[";",";",";","L8-419","2\\11\\21","GND","403\\19"]
[";",";",";","L8-420","2\\11\\22",null,"403\\20"]
[";",";",";","L8-421","2\\11\\23",null,"403\\21"]
[";",";",";","L8-422","2\\11\\24",null,"403\\22"]
["E 42.0"," ----SPARE------- "," ----SPARE------- ","L8-423","2\\11\\25",null,"403\\23"]
["E 42.1"," ----SPARE------- "," ----SPARE------- ","L8-424","2\\11\\26",null,"403\\24"]
["E 42.2"," ----SPARE------- "," ----SPARE------- ","L8-425","2\\11\\27",null,"403\\25"]
["E 42.3","MP156-1 MOTOR LOOPT (SEAC) ","MP156-1 MOTOR LOOPT (SEAC) ","L8-426","2\\11\\28",null,"403\\26"]
["E 42.4"," ----SPARE------- "," ----SPARE------- ","L8-427","2\\11\\29",null,"403\\27"]
["E 42.5"," ----SPARE------- "," ----SPARE------- ","L8-428","2\\11\\30",null,"403\\28"]
["E 42.6"," ----SPARE------- "," ----SPARE------- ","L8-429","2\\11\\31",null,"403\\29"]
["E 42.7"," ----SPARE------- "," ----SPARE------- ","L8-430","2\\11\\32",null,"403\\30"]
[";",";",";","L8-431","2\\11\\33",null,"403\\31"]
["E 43.0"," ----SPARE------- "," ----SPARE------- ","L8-432","2\\11\\34",null,"403\\32"]
["E 43.1"," ----SPARE------- "," ----SPARE------- ","L8-433","2\\11\\35",null,"403\\33"]
["E 43.2","TS172 H TEMP ROOKGAS UITL.C150 (SEAC) ","TS172 H TEMP ROOKGAS UITL.C150 (SEAC) ","L8-434","2\\11\\36",null,"403\\34"]
["E 43.3"," ----SPARE------- "," ----SPARE------- ","L8-435","2\\11\\37",null,"403\\35"]
["E 43.4"," ----SPARE------- "," ----SPARE------- ","L8-436","2\\11\\38",null,"403\\36"]
["E 43.5"," ----SPARE------- "," ----SPARE------- ","L8-437","2\\11\\39",null,"403\\37"]
["E 43.6","LS815-2 LL NIVO C815 ","LS815-2 LL NIVO C815","L8-438","2\\11\\40",null,"403\\38"]
["E 43.7"," ----SPARE------- "," ----SPARE------- ","L8-439","2\\11\\41",null,"403\\39"]
[";",";",";","L8-440","2\\11\\42",null,"403\\PE"]
[";",";",";","L8-441","2\\12\\3","24VDC","404\\1"]
["E 44.0 "," ----SPARE------- "," ----SPARE------- ","L8-442","2\\12\\4",null,"404\\2"]
["E 44.1","FS155156 KOELWATER NIET AANWEZIG "," ----SPARE------- ","L8-443","2\\12\\5",null,"404\\3"]
["E 44.2"," ----SPARE------- "," ----SPARE------- ","L8-444","2\\12\\6",null,"404\\4"]
["E 44.3","MM831 MOTOR LOOPT (VACUUMFILTER) ","ROERWERK TANK 2 IN BEDRIJF              MGSO4","L8-445","2\\12\\7",null,"404\\5","pag.0013"]
["E 44.4","MM830 MOTOR LOOPT (VACUUMFILTER) ","ROERWERK TANK 1 IN BEDRIJF              MGSO4","L8-446","2\\12\\8",null,"404\\6","pag.0013"]
["E 44.5"," ----SPARE------- "," ----SPARE------- ","L8-447","2\\12\\9",null,"404\\7"]
["E 44.6","XEV182 OPEN FEEDBACK "," ----SPARE------- ","L8-448","2\\12\\10",null,"404\\8"]
["E 44.7","TS169 TEMPERATUUR BED 1 ","TS169 TEMPERATUUR BED 2","L8-449","2\\12\\11",null,"404\\9"]
[";",";",";","L8-450","2\\12\\12",null,"404\\10"]
["E 45.0"," ----SPARE------- "," ----SPARE------- ","L8-451","2\\12\\13",null,"404\\11"]
["E 45.1"," ----SPARE------- "," ----SPARE------- ","L8-452","2\\12\\14",null,"404\\12"]
["E 45.2"," ----SPARE------- "," ----SPARE------- ","L8-453","2\\12\\15",null,"404\\13"]
["E 45.3"," ----SPARE------- "," ----SPARE------- ","L8-454","2\\12\\16",null,"404\\14"]
["E 45.4","PS820-1 PRE-OX. VENTILATOR K820A HOOG ","PS820-1 PRE-OX. VENTILATOR K820A HOOG ","L8-455","2\\12\\17",null,"404\\15"]
["E 45.5","PS820-3 PRE-OX. VENTILATOR K820B HOOG ","PS820-3 PRE-OX. VENTILATOR K820B HOOG ","L8-456","2\\12\\18",null,"404\\16"]
["E 45.6"," ----SPARE------- "," ----SPARE------- ","L8-457","2\\12\\19",null,"404\\17"]
["E 45.7"," ----SPARE------- "," ----SPARE------- ","L8-458","2\\12\\20",null,"404\\18"]
[";",";",";","L8-459","2\\12\\21","GND","404\\19"]
[";",";",";","L8-460","2\\12\\22",null,"404\\20"]
[";",";",";","L8-461","2\\12\\23",null,"404\\21"]
[";",";",";","L8-462","2\\12\\24",null,"404\\22"]
["E 46.0","ES.. NOODSTOP KETELBESTURING ","ES.. NOODSTOP KETELBESTURING ","L8-463","2\\12\\25",null,"404\\23"]
["E 46.1","1K17 SPANNING KETELBEST. AANWEZIG ","1K17 SPANNING KETELBEST. AANWEZIG ","L8-464","2\\12\\26",null,"404\\24"]
["E 46.2","PS151 H DRUK STOOM > 16 BAR "," ----SPARE------- ","L8-465","2\\12\\27",null,"404\\25"]
["E 46.3","FS152 WATERSTROOM SECTIE 1 "," ----SPARE------- ","L8-466","2\\12\\28",null,"404\\26"]
["E 46.4","FS153 WATERSTROOM SECTIE 2 "," ----SPARE------- ","L8-467","2\\12\\29",null,"404\\27"]
["E 46.5","FS154 VOEDING CIRC. P150 "," ----SPARE------- ","L8-468","2\\12\\30",null,"404\\28"]
["E 46.6","4K13 AANV.KETELVOORW. VOLDAAN ","4K13 AANV.KETELVOORW. VOLDAAN ","L8-469","2\\12\\31",null,"404\\29"]
["E 46.7","LS154 HH NIVO V150 HOOFDDRUM "," ----SPARE------- ","L8-470","2\\12\\32",null,"404\\30"]
[";",";",";","L8-471","2\\12\\33",null,"404\\31"]
["E 47.0","LS155 HH NIVO V150 NEVENDRUM "," ----SPARE------- ","L8-472","2\\12\\34",null,"404\\32"]
["E 47.1","TS169 HH TEMP BED 1 ","TS169 HH TEMP BED 1","L8-473","2\\12\\35",null,"404\\33"]
["E 47.2","TS170 HH TEMP BED 2 ","TS170 HH TEMP BED 2","L8-474","2\\12\\36",null,"404\\34"]
["E 47.3","dPS160 BEDHOOGTE < MIN. ","dPS160 BEDHOOGTE < MIN. ","L8-475","2\\12\\37",null,"404\\35"]
["E 47.4","XS.. STORING WATCHDOG PLC ","XS.. STORING WATCHDOG PLC ","L8-476","2\\12\\38",null,"404\\36"]
["E 47.5","PS163 H DRUK VUURHAARD ","PS163 H DRUK VUURHAARD ","L8-477","2\\12\\39",null,"404\\37"]
["E 47.6","PS180 L DRUK STUURLUCHT ","PS180 L DRUK STUURLUCHT ","L8-478","2\\12\\40",null,"404\\38"]
["E 47.7","PS174 L DRUK AANST.LUCHT ","PS174 L DRUK AANST.LUCHT ","L8-479","2\\12\\41",null,"404\\39"]
[null,null,null,"L8-480","2\\12\\42",null,"404\\PE"]
[";",";",";","L8-481","2\\13\\3","24VDC","405\\1"]
["E 48.0","PS171-1 L DRUK GAS ","PS171-1 L DRUK GAS ","L8-482","2\\13\\4",null,"405\\2"]
["E 48.1","PS171-2 H DRUK GAS ","PS171-2 H DRUK GAS ","L8-483","2\\13\\5",null,"405\\3"]
["E 48.2","XZS168/169 HOOFDGASVENTIEL NIET GESLOTEN ","XZS168/169 HOOFDGASVENTIEL NIET GESLOTEN ","L8-484","2\\13\\6",null,"405\\4"]
["E 48.3","FS198199 VERBRANDINGSLUCHTFLOW < MIN. ","FS198199 VERBRANDINGSLUCHTFLOW < MIN. ","L8-485","2\\13\\7",null,"405\\5"]
["E 48.4","TZS183 GASKLEP BED NIET IN STAND POS. ","TZS183 GASKLEP BED NIET IN STAND POS. ","L8-486","2\\13\\8",null,"405\\6"]
["E 48.5","TZS184 GASKLEP BED NIET IN STAND POS. ","TZS184 GASKLEP BED NIET IN STAND POS. ","L8-487","2\\13\\9",null,"405\\7"]
["E 48.6","FS198199 SPOELLUCHTFLOW < 90% ","FS198199 SPOELLUCHTFLOW < 90% ","L8-488","2\\13\\10",null,"405\\8"]
["E 48.7","TS158-1/159-1 SPOELEN OVERBR. T=600 GRD ","TS158-1/159-1 SPOELEN OVERBR. T=600 GRD ","L8-489","2\\13\\11",null,"405\\9"]
[";",";",";","L8-490","2\\13\\12","NC","405\\10"]
["E 49.0 ","9K16/K18 VOORW. CIRCUIT GESLOTEN ","9K16/K18 VOORW. CIRCUIT GESLOTEN ","L8-491","2\\13\\13",null,"405\\11"]
["E 49.1","10K3 VLAM STORING ","10K3 VLAM STORING ","L8-492","2\\13\\14",null,"405\\12"]
["E 49.2","10K10 REGELVRIJGAVE TIC AUTO ","10K10 REGELVRIJGAVE TIC AUTO ","L8-493","2\\13\\15",null,"405\\13"]
["E 49.3","10K12 REGELVRIJGAVE ","10K12 REGELVRIJGAVE ","L8-494","2\\13\\16",null,"405\\14"]
["E 49.4","10K14 TEST VERBR.LUCHT DRUKSCHAKELAAR ","10K14 TEST VERBR.LUCHT DRUKSCHAKELAAR ","L8-495","2\\13\\17",null,"405\\15"]
["E 49.5","11K4 PROGRAMMA STARTBEREID ","11K4 PROGRAMMA STARTBEREID ","L8-496","2\\13\\18",null,"405\\16"]
["E 49.6","dPS158 VERBR.LUCHT < MIN ","dPS158 VERBR.LUCHT < MIN ","L8-497","2\\13\\19",null,"405\\17"]
["E 49.7","XS173 GASLEK HOOFDVENTIEL ","XS173 GASLEK HOOFDVENTIEL ","L8-498","2\\13\\20",null,"405\\18"]
[";",";",";","L8-499","2\\13\\21","GND","405\\19"]
[";",";",";","L8-500","2\\13\\22","NC","405\\20"]
[";",";",";","L8-501","2\\13\\23","NC","405\\21"]
[";",";",";","L8-502","2\\13\\24","NC","405\\22"]
["E 50.0","12K3/K7 REGELING NAAR SPOELSTAND (90% FL ","12K3/K7 REGELING NAAR SPOELSTAND (90% FL ","L8-503","2\\13\\25",null,"405\\23"]
["E 50.1","12K3 REGELING NAAR SPOELSTAND ","12K3 REGELING NAAR SPOELSTAND ","L8-504","2\\13\\26",null,"405\\24"]
["E 50.2","12K7 SPOELTIJD LOOPT (5 MIN.) ","12K7 SPOELTIJD LOOPT (5 MIN.) ","L8-505","2\\13\\27",null,"405\\25"]
["E 50.3","12K13/K18 REGELING NAAR START STAND ","12K13/K18 REGELING NAAR START STAND ","L8-506","2\\13\\28",null,"405\\26"]
["E 50.4","12K3/K18 PROGRAMMA LOOPT ","12K3/K18 PROGRAMMA LOOPT ","L8-507","2\\13\\29",null,"405\\27"]
["E 50.5","13K3/K5 AANST.BRANDERS CONTINU ","13K3/K5 AANST.BRANDERS CONTINU ","L8-508","2\\13\\30",null,"405\\28"]
["E 50.6","13K8 ONTSTEKING IN ","13K8 ONTSTEKING IN ","L8-509","2\\13\\31",null,"405\\29"]
["E 50.7","XEV168 HOOFDVENTIEL VA1 OPEN ","XEV168 HOOFDVENTIEL VA1 OPEN ","L8-510","2\\13\\32",null,"405\\30"]
[";",";",";","L8-511","2\\13\\33","NC","405\\31"]
["E 51.0","XEV169/170/171 HOOFDVENTIELEN VA2,VA3-1, ","XEV169/170/171 HOOFDVENTIELEN VA2,VA3-1, ","L8-512","2\\13\\34",null,"405\\32"]
["E 51.1","BR152 AANST.BRANDER 2 IN STORING ","BR152 AANST.BRANDER 2 IN STORING ","L8-513","2\\13\\35",null,"405\\33"]
["E 51.2","BR153 AANST.BRANDER 1 IN STORING ","BR153 AANST.BRANDER 1 IN STORING ","L8-514","2\\13\\36",null,"405\\34"]
["E 51.3","15K7 HOOFDVLAM AANWEZIG ","15K7 HOOFDVLAM AANWEZIG ","L8-515","2\\13\\37",null,"405\\35"]
["E 51.4","XEV164/165/166 AANST.VENTIELEN OPEN ","XEV164/165/166 AANST.VENTIELEN OPEN ","L8-516","2\\13\\38",null,"405\\36"]
["E 51.5","XEV170 HOOFDBRANDERS BED 2 UIT ","XEV170 HOOFDBRANDERS BED 2 UIT ","L8-517","2\\13\\39",null,"405\\37"]
["E 51.6","XEV171 HOOFDBRANDERS BED 1 UIT ","XEV171 HOOFDBRANDERS BED 1 UIT ","L8-518","2\\13\\40",null,"405\\38"]
["E 51.7","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-519","2\\13\\41",null,"405\\39"]
[";",";",";","L8-520","2\\13\\42",null,"405\\PE"]
["DIGITALE UITGANGEN",null,null,"HLRVD",null,"INTERFACE"]
[" 5 KAARTEN A 32 UITGANGEN SPARE = 30 % ",null,null,null,"R/K/Aans","RELAIS","KABEL/NR"]
[";",";",null,"L8-521","2\\14\\3","24VDC","406\\1"]
["A 0.0","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-522","2\\14\\4",37102,"406\\2"]
["A 0.1","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-523","2\\14\\5",37104,"406\\3"]
["A 0.2","XEV818 OPEN ","XEV818 OPEN ","L8-524","2\\14\\6",37106,"406\\4"]
["A 0.3","MK802 START"," ----SPARE------- ","L8-525","2\\14\\7",37108,"406\\5"]
["A 0.4"," ----SPARE------- "," ----SPARE------- ","L8-526","2\\14\\8",37110,"406\\6"]
["A 0.5","MA802 START"," ----SPARE------- ","L8-527","2\\14\\9",37112,"406\\7"]
["A 0.6"," ----SPARE------- "," ----SPARE------- ","L8-528","2\\14\\10",37114,"406\\8"]
["A 0.7"," ----SPARE------- "," ----SPARE------- ","L8-529","2\\14\\11",37116,"406\\9"]
[";",";",";","L8-530","2\\14\\12",null,"406\\10"]
["A 1.0","MK129 START "," ----SPARE------- ","L8-531","2\\14\\13",37202,"406\\11"]
["A 1.1","MF129 START "," ----SPARE------- ","L8-532","2\\14\\14",37204,"406\\12"]
["A 1.2","MA129 START"," ----SPARE------- ","L8-533","2\\14\\15",37206,"406\\13"]
["A 1.3","MA130 START"," ----SPARE------- ","L8-534","2\\14\\16",37208,"406\\14"]
["A 1.4","MK132 START"," ----SPARE------- ","L8-535","2\\14\\17",37210,"406\\15"]
["A 1.5"," ----SPARE------- "," ----SPARE------- ","L8-536","2\\14\\18",37212,"406\\16"]
["A 1.6","MA128 START "," ----SPARE------- ","L8-537","2\\14\\19",37214,"406\\17"]
["A 1.7","MA131 START "," ----SPARE------- ","L8-538","2\\14\\20",37216,"406\\18"]
[";",";",";","L8-539","2\\14\\21","GND","406\\19"]
[";",";",";","L8-540","2\\14\\22",null,"406\\20"]
[";",";",";","L8-541","2\\14\\23",null,"406\\21"]
[";",";",";","L8-542","2\\14\\24","24VDC","406\\22"]
["A 2.0","MK134 START "," ----SPARE------- ","L8-543","2\\14\\25",37302,"406\\23"]
["A 2.1","MF134 START "," ----SPARE------- ","L8-544","2\\14\\26",37304,"406\\24"]
["A 2.2","MA134 START"," ----SPARE------- ","L8-545","2\\14\\27",37306,"406\\25"]
["A 2.3","MA135 START"," ----SPARE------- ","L8-546","2\\14\\28",37308,"406\\26"]
["A 2.4","MK137 START"," ----SPARE------- ","L8-547","2\\14\\29",37310,"406\\27"]
["A 2.5"," ----SPARE------- "," ----SPARE------- ","L8-548","2\\14\\30",37312,"406\\28"]
["A 2.6","MA137 START"," ----SPARE------- ","L8-549","2\\14\\31",37314,"406\\29"]
["A 2.7","MA133 START"," ----SPARE------- ","L8-550","2\\14\\32",37316,"406\\30"]
[";",";",";","L8-551","2\\14\\33",null,"406\\31"]
["A 3.0","MA140 START"," ----SPARE------- ","L8-552","2\\14\\34",37402,"406\\32"]
["A 3.1","MA136 START "," ----SPARE------- ","L8-553","2\\14\\35",37404,"406\\33"]
["A 3.2","MK128 START "," ----SPARE------- ","L8-554","2\\14\\36",37406,"406\\34"]
["A 3.3","MK131 START "," ----SPARE------- ","L8-555","2\\14\\37",37408,"406\\35"]
["A 3.4"," ----SPARE------- "," ----SPARE------- ","L8-556","2\\14\\38",37410,"406\\36"]
["A 3.5"," ----SPARE------- "," ----SPARE------- ","L8-557","2\\14\\39",37412,"406\\37"]
["A 3.6"," ----SPARE------- "," ----SPARE------- ","L8-558","2\\14\\40",37414,"406\\38"]
["A 3.7"," ----SPARE------- "," ----SPARE------- ","L8-559","2\\14\\41",37416,"406\\39"]
[";",";",";","L8-560","2\\14\\42",null,"406\\PE"]
[";",";",";","L8-561","2\\15\\3","24VDC","407\\1"]
["A 4.0","MP800 START ","MP800 START ","L8-562","2\\15\\4",37502,"407\\2"]
["A 4.1","START HOOFDBRANDERS ","START HOOFDBRANDERS ","L8-563","2\\15\\5",37504,"407\\3"]
["A 4.2","MP802A START","MP802A START","L8-564","2\\15\\6",37506,"407\\4"]
["A 4.3","MA161 START ","MA161 START ","L8-565","2\\15\\7",37508,"407\\5"]
["A 4.4","KLEPSTURING XEV163-24","DOEKENFILTER KLEP 24","L8-566","2\\15\\8",37510,"407\\6","X163/8"]
["A 4.5","XEV108 OPEN "," ----SPARE------- ","L8-567","2\\15\\9",37512,"407\\7"]
["A 4.6"," ----SPARE------- "," ----SPARE------- ","L8-568","2\\15\\10",37514,"407\\8"]
["A 4.7"," ----SPARE------- "," ----SPARE------- ","L8-569","2\\15\\11",37516,"407\\9"]
[";",";",";","L8-570","2\\15\\12",null,"407\\10"]
["A 5.0","VERWARMING KOP DOEKENFILTER AAN ","VERWARMING KOP DOEKENFILTER AAN ","L8-571","2\\15\\13",37602,"407\\11"]
["A 5.1","MP950 START ","MP950 START ","L8-572","2\\15\\14",37604,"407\\12"]
["A 5.2"," ----SPARE------- "," ----SPARE------- ","L8-573","2\\15\\15",37606,"407\\13"]
["A 5.3","MK820B START ","MK820B START ","L8-574","2\\15\\16",37608,"407\\14"]
["A 5.4","MP910A START ","MP910A START ","L8-575","2\\15\\17",37610,"407\\15"]
["A 5.5","MP910S START ","MP910S START ","L8-576","2\\15\\18",37612,"407\\16"]
["A 5.6","MM802 START ","MM802 START ","L8-577","2\\15\\19",37614,"407\\17"]
["A 5.7","MA157 START ","XEV157 OPEN","L8-578","2\\15\\20",37616,"407\\18"]
[";",";",";","L8-579","2\\15\\21","GND","407\\19"]
[";",";",";","L8-580","2\\15\\22",null,"407\\20"]
[";",";",";","L8-581","2\\15\\23",null,"407\\21"]
[";",";",";","L8-582","2\\15\\24","24VDC","407\\22"]
["A 6.0","MA150 START ","MA150 START ","L8-583","2\\15\\25",37702,"407\\23"]
["A 6.1","MA151 START ","MA151 START ","L8-584","2\\15\\26",37704,"407\\24"]
["A 6.2"," ----SPARE------- "," ----SPARE------- ","L8-585","2\\15\\27",37706,"407\\25"]
["A 6.3"," ----SPARE------- "," ----SPARE------- ","L8-586","2\\15\\28",37708,"407\\26"]
["A 6.4"," ----SPARE------- "," ----SPARE------- ","L8-587","2\\15\\29",37710,"407\\27"]
["A 6.5","MA182 START",null,"L8-588","2\\15\\30",37712,"407\\28"]
["A 6.6","MA158 START ","MA152 START ","L8-589","2\\15\\31",37714,"407\\29"]
["A 6.7","K9108 ","MA160.3 START ","L8-590","2\\15\\32",37716,"407\\30"]
[";",";",";","L8-591","2\\15\\33",null,"407\\31"]
["A 7.0 ","MA160-1 START ","MA160-1 START ","L8-592","2\\15\\34",37802,"407\\32"]
["A 7.1"," ----SPARE------- "," ----SPARE------- ","L8-593","2\\15\\35",37804,"407\\33"]
["A 7.2","MA179 START ","MA179 START ","L8-594","2\\15\\36",37806,"407\\34"]
["A 7.3","MA160-2 START ","MA160-2 START ","L8-595","2\\15\\37",37808,"407\\35"]
["A 7.4"," ----SPARE------- "," ----SPARE------- ","L8-596","2\\15\\38",37810,"407\\36"]
["A 7.5","MA168 START","MA153 START ","L8-597","2\\15\\39",37812,"407\\37"]
["A 7.6","MK150 START ","MK150 START ","L8-598","2\\15\\40",37814,"407\\38"]
["A 7.7","MK151.1 START ","MK151.1 START ","L8-599","2\\15\\41",37816,"407\\39"]
[null,null,null,"L8-600","2\\15\\42",null,"407\\PE"]
[";",";",";","L8-601","2\\16\\3","24VDC","408\\1"]
["A 8.0","MK152 START ","MK152 START ","L8-602","2\\16\\4",37902,"408\\2"]
["A 8.1","MA173 START ","MP804 START ","L8-603","2\\16\\5",37904,"408\\3"]
["A 8.2","MA156 START ","MA152.1 START ","L8-604","2\\16\\6",37906,"408\\4"]
["A 8.3","MA178 START "," ----SPARE------- ","L8-605","2\\16\\7",37908,"408\\5"]
["A 8.4"," ----SPARE------- "," ----SPARE------- ","L8-606","2\\16\\8",37910,"408\\6"]
["A 8.5","MK158 START ","MK910 START ","L8-607","2\\16\\9",37912,"408\\7"]
["A 8.6","K9004 MCC607B","MK151.2 START ","L8-608","2\\16\\10",37914,"408\\8"]
["A 8.7","MP151 START ","MP815.2 START ","L8-609","2\\16\\11",37916,"408\\9"]
[";",";",";","L8-610","2\\16\\12",null,"408\\10"]
["A 9.0","4K1A SALDEN KAST PLC RUIMTE","MK818.2 START ","L8-611","2\\16\\13",38002,"408\\11","MK818-2"]
["A 9.1","MS159 START"," ----SPARE------- ","L8-612","2\\16\\14",38004,"408\\12"]
["A 9.2"," ----SPARE------- "," ----SPARE------- ","L8-613","2\\16\\15",38006,"408\\13"]
["A 9.3","MA156.1 START ",null,"L8-614","2\\16\\16",38008,"408\\14"]
["A 9.4","KLEPSTURING XEV163-1 & XEV1631.1","DOEKENFILTER KLEP 1 ","L8-615","2\\16\\17",38010,"408\\15","X163/2"]
["A 9.5","KLEPSTURING XEV163-2 ","DOEKENFILTER KLEP 2 ","L8-616","2\\16\\18",38012,"408\\16","X163/2"]
["A 9.6","KLEPSTURING XEV163-3 ","DOEKENFILTER KLEP 3 ","L8-617","2\\16\\19",38014,"408\\17","X163/2"]
["A 9.7","KLEPSTURING XEV163-4","DOEKENFILTER KLEP 4 ","L8-618","2\\16\\20",38016,"408\\18","X163/3"]
[";",";",";","L8-619","2\\16\\21","GND","408\\19"]
[";",";",";","L8-620","2\\16\\22",null,"408\\20"]
[";",";",";","L8-621","2\\16\\23",null,"408\\21"]
[";",";",";","L8-622","2\\16\\24","24VDC","408\\22"]
["A 10.0"," ----SPARE-------"," ----SPARE-------","L8-623","2\\16\\25",38102,"408\\23"]
["A 10.1"," ----SPARE------- "," ----SPARE------- ","L8-624","2\\16\\26",38104,"408\\24"]
["A 10.2"," ----SPARE------- "," ----SPARE------- ","L8-625","2\\16\\27",38106,"408\\25"]
["A 10.3","MA168.2 START ","MA151.1 START ","L8-626","2\\16\\28",38108,"408\\26"]
["A 10.4","MM804 START","MM804 START","L8-627","2\\16\\29",38110,"408\\27"]
["A 10.5","MP805 START ","MP805 START ","L8-628","2\\16\\30",38112,"408\\28"]
["A 10.6","MP815 START ","MP815.1 START ","L8-629","2\\16\\31",38114,"408\\29"]
["A 10.7"," ----SPARE------- "," ----SPARE------- ","L8-630","2\\16\\32",38116,"408\\30"]
[";",";",";","L8-631","2\\16\\33",null,"408\\31"]
["A 11.0","MP816A START ","MP816A START ","L8-632","2\\16\\34",38202,"408\\32"]
["A 11.1","MP816B START ","MP816B START ","L8-633","2\\16\\35",38204,"408\\33"]
["A 11.2"," ----SPARE------- "," ----SPARE------- ","L8-634","2\\16\\36",38206,"408\\34"]
["A 11.3"," ----SPARE------- "," ----SPARE------- ","L8-635","2\\16\\37",38208,"408\\35"]
["A 11.4","KLEPSTURING XEV163-23","DOEKENFILTER KLEP 23","L8-636","2\\16\\38",38210,"408\\36","X163/8"]
["A 11.5","MP816C START ","MP816C START ","L8-637","2\\16\\39",38212,"408\\37"]
["A 11.6"," ----SPARE------- "," ----SPARE------- ","L8-638","2\\16\\40",38214,"408\\38"]
["A 11.7"," ----SPARE------- "," ----SPARE------- ","L8-639","2\\16\\41",38216,"408\\39"]
[";",";",";","L8-640","2\\16\\42",null,"408\\PE"]
[";",";",";","L8-641","2\\17\\3","24VDC","409\\1"]
["A 12.0","CLAXON/ZWAAILICHT ","CLAXON/ZWAAILICHT ","L8-642","2\\17\\4",38302,"409\\2"]
["A 12.1"," ----SPARE------- "," ----SPARE------- ","L8-643","2\\17\\5",38304,"409\\3"]
["A 12.2"," ----SPARE------- "," ----SPARE------- ","L8-644","2\\17\\6",38306,"409\\4"]
["A 12.3"," ----SPARE------- "," ----SPARE------- ","L8-645","2\\17\\7",38308,"409\\5"]
["A 12.4"," ----SPARE------- "," ----SPARE------- ","L8-646","2\\17\\8",38310,"409\\6"]
["A 12.5","MP1001 START "," ----SPARE------- ","L8-647","2\\17\\9",38312,"409\\7"]
["A 12.6","XPV1008 OPEN "," ----SPARE------- ","L8-648","2\\17\\10",38314,"409\\8"]
["A 12.7","VRIJGAVE VERWARMING VASTVERF "," ----SPARE------- ","L8-649","2\\17\\11",38316,"409\\9"]
[";",";",";","L8-650","2\\17\\12",null,"409\\10"]
["A 13.0"," ----SPARE------- "," ----SPARE------- ","L8-651","2\\17\\13",38402,"409\\11"]
["A 13.1","WATCHDOG PLC STORING ","WATCHDOG PLC STORING ","L8-652","2\\17\\14",38404,"409\\12"]
["A 13.2","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-653","2\\17\\15",38406,"409\\13"]
["A 13.3","xxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxx ","L8-654","2\\17\\16",38408,"409\\14"]
["A 13.4","KLEPSTURING XEV163-5 ","DOEKENFILTER KLEP 5 ","L8-655","2\\17\\17",38410,"409\\15","X163/3"]
["A 13.5","KLEPSTURING XEV163-6 ","DOEKENFILTER KLEP 6 ","L8-656","2\\17\\18",38412,"409\\16","X163/3"]
["A 13.6","MK172 START-PULS ","MK172 START-PULS ","L8-657","2\\17\\19",38414,"409\\17"]
["A 13.7","MK172 STOP-PULS ","MK172 STOP-PULS ","L8-658","2\\17\\20",38416,"409\\18"]
[";",";",";","L8-659","2\\17\\21","GND","409\\19"]
[";",";",";","L8-660","2\\17\\22",null,"409\\20"]
[";",";",";","L8-661","2\\17\\23",null,"409\\21"]
[";",";",";","L8-662","2\\17\\24","24VDC","409\\22"]
["A 14.0","KLEPSTURING XEV163-11 ","DOEKENFILTER KLEP 11","L8-663","2\\17\\25",38502,"409\\23","X163/5"]
["A 14.1","MK175 START-PULS ","MK175 START-PULS ","L8-664","2\\17\\26",38504,"409\\24"]
["A 14.2","MK175 STOP-PULS ","MK175 STOP-PULS ","L8-665","2\\17\\27",38506,"409\\25"]
["A 14.3","MK818 START ","MK818 START ","L8-666","2\\17\\28",38508,"409\\26"]
["A 14.4","MP819 START ","MP819 START ","L8-667","2\\17\\29",38510,"409\\27"]
["A 14.5","MK819 START ","MK819 START ","L8-668","2\\17\\30",38512,"409\\28"]
["A 14.6","MK820A START ","MK820A START ","L8-669","2\\17\\31",38514,"409\\29"]
["A 14.7","XEV800 OPEN ","XEV800 OPEN ","L8-670","2\\17\\32",38516,"409\\30"]
[";",";",";","L8-671","2\\17\\33",null,"409\\31"]
["A 15.0","XEV815 OPEN ","XEV815 OPEN ","L8-672","2\\17\\34",38602,"409\\32"]
["A 15.1","MB154 START "," ----SPARE------- ","L8-673","2\\17\\35",38604,"409\\33"]
["A 15.2","MB155 START "," ----SPARE------- ","L8-674","2\\17\\36",38606,"409\\34"]
["A 15.3","XS150 START WATER CONTROL (SEAC) ","XS150 START WATER CONTROL (SEAC) ","L8-675","2\\17\\37",38608,"409\\35"]
["A 15.4","XS151 STOP WATER CONTROL (SEAC) ","XS151 STOP WATER CONTROL (SEAC) ","L8-676","2\\17\\38",38610,"409\\36"]
["A 15.5","XS115 START CONTROL SYSTEEM (SEAC) ","XS115 START CONTROL SYSTEEM (SEAC) ","L8-677","2\\17\\39",38612,"409\\37"]
["A 15.6"," ----SPARE------- (MA182 START ?) "," ----SPARE------- (MA182 START ?) ","L8-678","2\\17\\40",38614,"409\\38"]
["A 15.7","VRIJGAVE MGSO4-FILTER\f","VRIJGAVE MGSO4-FILTER\f","L8-679","2\\17\\41",38616,"409\\39"]
[null,null,null,"L8-680","2\\17\\42",null,"409\\PE"]
[";",";",";","L8-681","2\\18\\3","24VDC","410\\1","Br"]
["A 16.0","KLEPSTURING XEV163-12","DOEKENFILTER KLEP 12 ","L8-682","2\\18\\4",38702,"410\\2","X163/5"]
["A 16.1","KLEPSTURING XEV163-13 ","DOEKENFILTER KLEP 13 ","L8-683","2\\18\\5",38704,"410\\3","X163/5"]
["A 16.2","KLEPSTURING XEV163-14 ","DOEKENFILTER KLEP 14 ","L8-684","2\\18\\6",38706,"410\\4","X163/5"]
["A 16.3","KLEPSTURING XEV163-15 ","DOEKENFILTER KLEP 15 ","L8-685","2\\18\\7",38708,"410\\5","X163/6"]
["A 16.4","KLEPSTURING XEV163-16 ","DOEKENFILTER KLEP 16 ","L8-686","2\\18\\8",38710,"410\\6","X163/6"]
["A 16.5","KLEPSTURING XEV163-17 & XEV163-17.1","DOEKENFILTER KLEP 17 ","L8-687","2\\18\\9",38712,"410\\7","X163/6"]
["A 16.6","KLEPSTURING XEV163-18 ","DOEKENFILTER KLEP 18 ","L8-688","2\\18\\10",38714,"410\\8","X163/7"]
["A 16.7","RESET KETELTRIP (BRANDER) ","RESET KETELTRIP (BRANDER) ","L8-689","2\\18\\11",38716,"410\\9","Zw"]
[";",";",";","L8-690","2\\18\\12",null,"410\\10","Prs"]
["A 17.0","MA162 START ","MA162 START ","L8-691","2\\18\\13",38802,"410\\11","Grij/Rs"]
["A 17.1","KLEPSTURING XEV163-7 ","DOEKENFILTER KLEP 7 ","L8-692","2\\18\\14",38804,"410\\12","X163/3"]
["A 17.2","KLEPSTURING XEV163-8 ","DOEKENFILTER KLEP 8 ","L8-693","2\\18\\15",38806,"410\\13","X163/4"]
["A 17.3","KLEPSTURING XEV163-9 & XEV163-9.1","DOEKENFILTER KLEP 9 ","L8-694","2\\18\\16",38808,"410\\14","X163/4"]
["A 17.4","KLEPSTURING XEV163-10","DOEKENFILTER KLEP 10 ","L8-695","2\\18\\17",38810,"410\\15","X163/4"]
["A 17.5","AANV.KETELVOORW. VOLDAAN (BRANDER) ","AANV.KETELVOORW. VOLDAAN (BRANDER) ","L8-696","2\\18\\18",38812,"410\\16","Gl/Br"]
["A 17.6","KOELWATER AANWEZIG (BRANDER) ","KOELWATER AANWEZIG (BRANDER) ","L8-697","2\\18\\19",38814,"410\\17","Wt/Grij"]
["A 17.7","TEMP. BED 1 > 1000 GRD.C (BRANDER) ","TEMP. BED 1 > 1000 GRD.C (BRANDER) ","L8-698","2\\18\\20",38816,"410\\18","Grij/Br"]
[";",";",";","L8-699","2\\18\\21","GND","410\\19","Wt/Rs"]
[";",";",";","L8-700","2\\18\\22",null,"410\\20","Rs/Br"]
[";",";",";","L8-701","2\\18\\23",null,"410\\21","Wt/Bl"]
[";",";",";","L8-702","2\\18\\24","24VDC","410\\22","Br/Bl"]
["A 18.0","TEMP. BED 2 > 1000 GRD.C (BRANDER) ","TEMP. BED 2 > 1000 GRD.C (BRANDER) ","L8-703","2\\18\\25",38902,"410\\23","Wt/Rd"]
["A 18.1","BEDHOOGTE MINIMAAL (BRANDER) ","BEDHOOGTE MINIMAAL (BRANDER) ","L8-704","2\\18\\26",38904,"410\\24","Br/Rd"]
["A 18.2","OVERBR.SPOELEN T=550-600 GRD.C (BRANDER) ","OVERBR.SPOELEN T=550-600 GRD.C (BRANDER) ","L8-705","2\\18\\27",38906,"410\\25","Wt/Zw"]
["A 18.3","RESET VLAMSTORING (BRANDER) ","RESET VLAMSTORING (BRANDER) ","L8-706","2\\18\\28",38908,"410\\26","Br/Zw"]
["A 18.4","START/STOP BRANDERBEST. (BRANDER) ","START/STOP BRANDERBEST. (BRANDER) ","L8-707","2\\18\\29",38910,"410\\27","Grij/Gr"]
["A 18.5","AANST. BRANDERS CONTINU (BRANDER) ","AANST. BRANDERS CONTINU (BRANDER) ","L8-708","2\\18\\30",38912,"410\\28","Gl/Grij"]
["A 18.6","AANST. BRANDERS STOP (BRANDER) ","AANST. BRANDERS STOP (BRANDER) ","L8-709","2\\18\\31",38914,"410\\29","Rs/Gr"]
["A 18.7","HOOFDBRANDERS BED 1 AAN (BRANDER) ","HOOFDBRANDERS BED 1 AAN (BRANDER) ","L8-710","2\\18\\32",38916,"410\\30","Gl/Rs"]
[";",";",";","L8-711","2\\18\\33",null,"410\\31","Gr/Bl"]
["A 19.0","HOOFDBRANDERS BED 1 UIT (BRANDER) ","HOOFDBRANDERS BED 1 UIT (BRANDER) ","L8-712","2\\18\\34",39002,"410\\32","Gl/Bl"]
["A 19.1","HOOFDBRANDERS BED 2 AAN (BRANDER) ","HOOFDBRANDERS BED 2 AAN (BRANDER) ","L8-713","2\\18\\35",39004,"410\\33","Gr/Rd"]
["A 19.2","HOOFDBRANDERS BED 2 UIT (BRANDER) ","HOOFDBRANDERS BED 2 UIT (BRANDER) ","L8-714","2\\18\\36",39006,"410\\34","Ge/Rd"]
["A 19.3"," ----SPARE------- ","BEDRIJFSTEMPERATUUR (BRANDER)","L8-715","2\\18\\37",39008,"410\\35","Gr/Zw"]
["A 19.4","KLEPSTURING XEV163-19","DOEKENFILTER KLEP 19","L8-716","2\\18\\38",39010,"410\\36","X163/7"]
["A 19.5","KLEPSTURING XEV163-20","DOEKENFILTER KLEP 20","L8-717","2\\18\\39",39012,"410\\37","X163/7"]
["A 19.6","KLEPSTURING XEV163-21","DOEKENFILTER KLEP 21","L8-718","2\\18\\40",39014,"410\\38","X163/7"]
["A 19.7","KLEPSTURING XEV163-22","DOEKENFILTER KLEP 22","L8-719","2\\18\\41",39016,"410\\39","X163/8"]
[null,null,null,"L8-720","2\\18\\42",null,"410\\PE","Rs/Rd"]
[]
[null,"FUNCTIE","ANALOGE INGANGEN (PW) 13 KAARTEN"]
[null,null,null,"HLRVD","R/K/Aansl",null,"KABEL/NR"]
[";",";","REK 3 KAART 1","L4-1","3\\1\\3+24","24VDC","413\\1"]
["PW128+","NIVO CONDENSOR E-151 ","LT-150","L4-2","3\\1\\4","Ai+","413\\2"]
["PW128-","NIVO CONDENSOR E-151 ","LT-150","L4-3","3\\1\\6","Ai-","413\\3"]
["PW130+","NIVO HOOFDDRUM ","LT-151","L4-4","3\\1\\8","Ai+","413\\4"]
["PW130-","NIVO HOOFDDRUM ","LT-151","L4-5","3\\1\\10","Ai-","413\\5"]
["PW132+","NIVO NEVENDRUM (LT-152)","LT-152","L4-6","3\\1\\13","Ai+","413\\6"]
["PW132-","NIVO NEVENDRUM (LT-152)","LT-152","L4-7","3\\1\\15","Ai-","413\\7"]
["PW134+","NIVO BUFFERVAT V-151 (LT-153)","terugkoppeling frequentie omvormer K-818.2","L4-8","3\\1\\17","Ai+","413\\8"]
["PW134-","NIVO BUFFERVAT V-151 (LT-153)","terugkoppeling frequentie omvormer K-818.2","L4-9","3\\1\\19","Ai-","413\\9"]
[";",";",";","L4-10","3\\1\\21","COM","413\\10"]
["PW136+","NIVO KAT.BUNKER 1 (LT-167)","LT-167","L4-11","3\\1\\25","Ai+","413\\11"]
["PW136-","NIVO KAT.BUNKER 1 (LT-167)","LT-167","L4-12","3\\1\\27","Ai-","413\\12"]
["PW138+","NIVO KAT.BUNKER 2 (LT-168)","LT-168","L4-13","3\\1\\29","Ai+","413\\13"]
["PW138-","NIVO KAT.BUNKER 2 (LT-168)","LT-168","L4-14","3\\1\\31","Ai-","413\\14"]
["PW140+","NIVO KAT.BUNKER 3 & 4 (LT-169)","LT-169","L4-15","3\\1\\34","Ai+","413\\15"]
["PW140-","NIVO KAT.BUNKER 3 & 4 (LT-169)","LT-169","L4-16","3\\1\\36","Ai-","413\\16"]
["PW142+","pH METING AFVOER C-816","QT816A","L4-17","3\\1\\38","Ai+","413\\17"]
["PW142-","pH METING AFVOER C-816","QT816A","L4-18","3\\1\\40","Ai-","413\\PE"]
[";","ANALOGE INGANGEN","REK 3 KAART 2","L4-19","3\\2\\3+24","24VDC","414\\1"]
["PW144+","STOOMSTROOM (FT-150)",null,"L4-20","3\\2\\4","Ai+","414\\2"]
["PW144-","STOOMSTROOM (FT-150)",null,"L4-21","3\\2\\6","Ai-","414\\3"]
["PW146+","STOOMSTROOM NAAR V-151 (FT-151)",null,"L4-22","3\\2\\8","Ai+","414\\4"]
["PW146-","STOOMSTROOM NAAR V-151 (FT-151)",null,"L4-23","3\\2\\10","Ai-","414\\5"]
["PW148+","WATERSTROOM SECTIE 1 (FT-152)",null,"L4-24","3\\2\\13","Ai+","414\\6"]
["PW148-","WATERSTROOM SECTIE 1 (FT-152)",null,"L4-25","3\\2\\15","Ai-","414\\7"]
["PW150+","WATERSTROOM SECTIE 2 (FT-153)",null,"L4-26","3\\2\\17","Ai+","414\\8"]
["PW150-","WATERSTROOM SECTIE 2 (FT-153)",null,"L4-27","3\\2\\19","Ai-","414\\9"]
[";",";",";","L4-28","3\\2\\21","COM","414\\10"]
["PW152+","FLOW CONDENSAATPOMP P-151 (FT-157)",null,"L4-29","3\\2\\25","Ai+","414\\11"]
["PW152-","FLOW CONDENSAATPOMP P-151 (FT-157)",null,"L4-30","3\\2\\27","Ai-","414\\12"]
["PW154+","VERBR.LUCHTSTR.REG.LUVO 1 (FT-158)","FT-158","L4-31","3\\2\\29","Ai+","414\\13"]
["PW154-","VERBR.LUCHTSTR.REG.LUVO 1 (FT-158)","FT-158","L4-32","3\\2\\31","Ai-","414\\14"]
["PW156+","VERBR.LUCHTSTR.REG.LUVO 2 (FT-159)","FT-159","L4-33","3\\2\\34","Ai+","414\\15"]
["PW156-","VERBR.LUCHTSTR.REG.LUVO 2 (FT-159)","FT-159","L4-34","3\\2\\36","Ai-","414\\16"]
["PW158+","F816.2 (24VDC) - FT816 - FY816 (PS5104)","WASVLOEISTOF NAAR KOLOM C816 (FT816)","L4-35","3\\2\\38","Ai+","414\\17","F-816"]
["PW158-","F816.2 (24VDC) - FT816 - FY816 (PS5104)","WASVLOEISTOF NAAR KOLOM C816 (FT816)","L4-36","3\\2\\40","Ai-","414\\PE","F-816"]
[";","ANALOGE INGANGEN","REK 3 KAART 3","L4-37","3\\3\\3+24","24VDC","415\\1"]
["PW160+","F817.2(24VDC) - FT817 - FY817 (PS5104)","WASVLOEISTOF NAAR KOLOM C817 (FT817)","L4-38","3\\3\\4","Ai+","415\\2","F-817"]
["PW160-","F817.2(24VDC) - FT817 - FY817 (PS5104)","WASVLOEISTOF NAAR KOLOM C817 (FT817)","L4-39","3\\3\\6","Ai-","415\\3","F-817"]
["PW162+","F818.2(24VDC) - FT818 - FY818 (PS5104)","WASVLOEISTOF NAAR KOLOM C818 (FT818)","L4-40","3\\3\\8","Ai+","415\\4","F-818"]
["PW162-","F818.2(24VDC) - FT818 - FY818 (PS5104)","WASVLOEISTOF NAAR KOLOM C818 (FT818)","L4-41","3\\3\\10","Ai-","415\\5","F-818"]
["PW164+","PRODUCT TANK V-800A","LT800-1","L4-42","3\\3\\13","Ai+","415\\6"]
["PW164-","PRODUCT TANK V-800A","LT800-1","L4-43","3\\3\\15","Ai-","415\\7"]
["PW166+","GASFLOW BED 1","FT171","L4-44","3\\3\\17","Ai+","415\\8"]
["PW166-","GASFLOW BED 1","FT171","L4-45","3\\3\\19","Ai-","415\\9"]
[";",";",";","L4-46","3\\3\\21","COM","415\\10"]
["PW168+","GASFLOW BED 2","FT172","L4-47","3\\3\\25","Ai+","415\\11"]
["PW168-","GASFLOW BED 2","FT172","L4-48","3\\3\\27","Ai-","415\\12"]
["PW170+","LUCHT NAAR AANSTEEKBRANDERS","FIT173","L4-49","3\\3\\29","Ai+","415\\13"]
["PW170-","LUCHT NAAR AANSTEEKBRANDERS","FIT173","L4-50","3\\3\\31","Ai-","415\\14"]
["PW172+","SPOELLUCHT BRANDERS","FIT176","L4-51","3\\3\\34","Ai+","415\\15"]
["PW172-","SPOELLUCHT BRANDERS","FIT176","L4-52","3\\3\\36","Ai-","415\\16"]
["PW174+","pH METING AFVOER C-816","QT816B","L4-53","3\\3\\38","Ai+","415\\17"]
["PW174-","pH METING AFVOER C-816","QT816B","L4-54","3\\3\\40","Ai-","415\\PE"]
[";","ANALOGE INGANGEN","REK 3 KAART 4","L4-55","3\\4\\3+24","24VDC","416\\1"]
["PW176+","STOOMDRUK","PT150    (BRANDERS)","L4-56","3\\4\\4","Ai+","416\\2"]
["PW176-","STOOMDRUK","PT150    (BRANDERS)","L4-57","3\\4\\6","Ai-","416\\3"]
["PW178+","dP ROOSTERPLAAT BED 1","dPT156  (BRANDERS)","L4-58","3\\4\\8","Ai+","416\\4"]
["PW178-","dP ROOSTERPLAAT BED 1","dPT156  (BRANDERS)","L4-59","3\\4\\10","Ai-","416\\5"]
["PW180+","DRUK BED 1 & 2","dPT157","L4-60","3\\4\\13","Ai+","416\\6"]
["PW180-","DRUK BED 1 & 2","dPT157","L4-61","3\\4\\15","Ai-","416\\7"]
["PW182+","DRUK BED 1 & 2","dPT158","L4-62","3\\4\\17","Ai+","416\\8"]
["PW182-","DRUK BED 1 & 2","dPT158","L4-63","3\\4\\19","Ai-","416\\9"]
[";",";",";","L4-64","3\\4\\21","COM","416\\10"]
["PW184+","DRUK BED 1 & 2","dPT159","L4-65","3\\4\\25","Ai+","416\\11"]
["PW184-","DRUK BED 1 & 2","dPT159","L4-66","3\\4\\27","Ai-","416\\12"]
["PW186+","DRUK BED 1 & 2","dPT160","L4-67","3\\4\\29","Ai+","416\\13"]
["PW186-","DRUK BED 1 & 2","dPT160","L4-68","3\\4\\31","Ai-","416\\14"]
["PW188+","ROOSTERPLAAT BED 2","dPT161","L4-69","3\\4\\34","Ai+","416\\15"]
["PW188-","ROOSTERPLAAT BED 2","dPT161","L4-70","3\\4\\36","Ai-","416\\16"]
["PW190+","VUURHAARDDRUK METING (ONDERDRUK)","PT162","L4-71","3\\4\\38","Ai+","416\\17","P162"]
["PW190-","VUURHAARDDRUK METING (ONDERDRUK)","PT162","L4-72","3\\4\\40","Ai-","416\\PE","P162"]
[";","ANALOGE INGANGEN","REK 3 KAART 5","L4-73","3\\5\\3+24","24VDC","417\\1"]
["PW192+","DELTA DRUK CYCLOON","dPT165","L4-74","3\\5\\4","Ai+","417\\2"]
["PW192-","DELTA DRUK CYCLOON","dPT165","L4-75","3\\5\\6","Ai-","417\\3"]
["PW194+","DELTA DRUK DOEKENFILTER","dPT166","L4-76","3\\5\\8","Ai+","417\\4"]
["PW194-","DELTA DRUK DOEKENFILTER","dPT166","L4-77","3\\5\\10","Ai-","417\\5"]
["PW196+","pH METING AFVOER C-818","QT818B","L4-78","3\\5\\13","Ai+","417\\6"]
["PW196-","pH METING AFVOER C-818","QT818B","L4-79","3\\5\\15","Ai-","417\\7"]
["PW198+","pH METING AFVOER C-819","QT819A","L4-80","3\\5\\17","Ai+","417\\8"]
["PW198-","pH METING AFVOER C-819","QT819A","L4-81","3\\5\\19","Ai-","417\\9"]
[";",";",";","L4-82","3\\5\\21","COM","417\\10"]
["PW200+","pH METING AFVOER C-817","QT817A","L4-83","3\\5\\25","Ai+","417\\11"]
["PW200-","pH METING AFVOER C-817","QT817A","L4-84","3\\5\\27","Ai-","417\\12"]
["PW202+","XXXXXXXX","XXXXXXXX","L4-85","3\\5\\29","Ai+","417\\13"]
["PW202-","XXXXXXXX","XXXXXXXX","L4-86","3\\5\\31","Ai-","417\\14"]
["PW204+","XXXXXXXX","XXXXXXXX","L4-87","3\\5\\34","Ai+","417\\15"]
["PW204-","XXXXXXXX","XXXXXXXX","L4-88","3\\5\\36","Ai-","417\\16"]
["PW206+","XXXXXXXX","XXXXXXXX","L4-89","3\\5\\38","Ai+","417\\17"]
["PW206-","XXXXXXXX","XXXXXXXX","L4-90","3\\5\\40","Ai-","417\\PE"]
[";","ANALOGE INGANGEN","REK 3 KAART 6","L4-91","3\\6\\3+24","24VDC","418\\1"]
["PW208+","SPEED MA150","ST150","L4-92","3\\6\\4","Ai+","418\\2","S-150"]
["PW208-","SPEED MA150","ST150","L4-93","3\\6\\6","Ai-","418\\3","S-150"]
["PW210+","SPEED MA151   ","ST151","L4-94","3\\6\\8","Ai+","418\\4","S-151"]
["PW210-","SPEED MA151   ","ST151","L4-95","3\\6\\10","Ai-","418\\5","S-151"]
["PW212+","ZUURSTOFPERCENTAGE","QT150","L4-96","3\\6\\13","Ai+","418\\6"]
["PW212-","ZUURSTOFPERCENTAGE","QT150","L4-97","3\\6\\15","Ai-","418\\7"]
["PW214+","STOFDICHTHEID","QT151","L4-98","3\\6\\17","Ai+","418\\8"]
["PW214-","STOFDICHTHEID","QT151","L4-99","3\\6\\19","Ai-","418\\9"]
[";",";",";","L4-100","3\\6\\21","COM","418\\10"]
["PW216+","TEMPERATUUR NA CYCLOON","TT166","L4-101","3\\6\\25","Ai+","418\\11"]
["PW216-","TEMPERATUUR NA CYCLOON","TT166","L4-102","3\\6\\27","Ai-","418\\12"]
["PW218+","VERMOGENSMETING VERBR.L.VENT.","NT150","L4-103","3\\6\\29","Ai+","418\\13"]
["PW218-","VERMOGENSMETING VERBR.L.VENT.","NT150","L4-104","3\\6\\31","Ai-","418\\14"]
["PW220+","VERMOGENSMETING ROOKGASVENT.","NT151","L4-105","3\\6\\34","Ai+","418\\15"]
["PW220-","VERMOGENSMETING ROOKGASVENT.","NT151","L4-106","3\\6\\36","Ai-","418\\16"]
["PW222+","ROOKGASPERC. ONVERBRAND","QT512","L4-107","3\\6\\38","Ai+","418\\17"]
["PW222-","ROOKGASPERC. ONVERBRAND","QT152","L4-108","3\\6\\40","Ai-","418\\PE"]
[";","ANALOGE INGANGEN","REK 3 KAART 7","L4-109","3\\7\\3+24","24VDC","419\\1"]
["PW224+","pH METING AFVOER C-819","QT819B","L4-110","3\\7\\4","Ai+","419\\2"]
["PW224-","pH METING AFVOER C-819","QT819B","L4-111","3\\7\\6","Ai-","419\\3"]
["PW226+","pH METING AFVOER C-820","QT820A","L4-112","3\\7\\8","Ai+","419\\4"]
["PW226-","pH METING AFVOER C-820","QT820A","L4-113","3\\7\\10","Ai-","419\\5"]
["PW228+","pH METING AFVOER C-820","QT820B","L4-114","3\\7\\13","Ai+","419\\6"]
["PW228-","pH METING AFVOER C-820","QT820B","L4-115","3\\7\\15","Ai-","419\\7"]
["PW230+","DICHTHEID PREOX.VL.ST. V-820","QT820-2","L4-116","3\\7\\17","Ai+","419\\8"]
["PW230-","DICHTHEID PREOX.VL.ST. V-820","QT820-2","L4-117","3\\7\\19","Ai-","419\\9"]
[";",";",";","L4-118","3\\7\\21","COM","419\\10"]
["PW232+","SCRUBBER C-815","LT815-1","L4-119","3\\7\\25","Ai+","419\\11"]
["PW232-","SCRUBBER C-815","LT815-1","L4-120","3\\7\\27","Ai-","419\\12"]
["PW234+","XXXXXXXX","XXXXXXXX","L4-121","3\\7\\29","Ai+","419\\13"]
["PW234-","XXXXXXXX","XXXXXXXX","L4-122","3\\7\\31","Ai-","419\\14"]
["PW236+","XXXXXXXX","XXXXXXXX","L4-123","3\\7\\34","Ai+","419\\15"]
["PW236-","XXXXXXXX","XXXXXXXX","L4-124","3\\7\\36","Ai-","419\\16"]
["PW238+","XXXXXXXX","XXXXXXXX","L4-125","3\\7\\38","Ai+","419\\17"]
["PW238-","XXXXXXXX","XXXXXXXX","L4-126","3\\7\\40","Ai-","419\\PE"]
[]
[";","ANALOGE INGANGEN","REK 3 KAART 8","L4-127","3\\8\\3+24","24VDC","420\\1"]
["PW240+","HYDROXIDE OPSLAGTANK V-802","LT802-1","L4-128","3\\8\\4","Ai+","420\\2"]
["PW240-","HYDROXIDE OPSLAGTANK V-802","LT802-1","L4-129","3\\8\\6","Ai-","420\\3"]
["PW242+","FINALOX.TANK V-804","LT804-1","L4-130","3\\8\\8","Ai+","420\\4"]
["PW242-","FINALOX.TANK V-804","LT804-1","L4-131","3\\8\\10","Ai-","420\\5"]
["PW244+","FINALOX.UITLAAT V-819","LT170 NIVOMETING VAT 156            (SEAC)","L4-132","3\\8\\13","Ai+","420\\6","L170"]
["PW244-","FINALOX.UITLAAT V-819","LT170 NIVOMETING VAT 156            (SEAC)","L4-133","3\\8\\15","Ai-","420\\7","L170"]
["PW246+","F820.1  (230VAC)  ---  LT820.1","LT820-1  PRE OXIDATIE TANK VAT 820","L4-134","3\\8\\17","Ai+","420\\8","L820"]
["PW246-","F820.1  (230VAC)  ---  LT820.1","LT820-1  PRE OXIDATIE TANK VAT 820","L4-135","3\\8\\19","Ai-","420\\9","L820"]
[";",";",";","L4-136","3\\8\\21","COM","420\\10"]
["PW248+","ROOKGAS NAAR KOELER Z-815","PT812","L4-137","3\\8\\25","Ai+","420\\11"]
["PW248-","ROOKGAS NAAR KOELER Z-815","PT812","L4-138","3\\8\\27","Ai-","420\\12"]
["PW250+","SO2 METING GEWASSEN ROOKGAS","QT811-1","L4-139","3\\8\\29","Ai+","420\\13"]
["PW250-","SO2 METING GEWASSEN ROOKGAS","QT811-1","L4-140","3\\8\\31","Ai-","420\\14"]
["PW252+","pH METING AFVOER C-817","QT817B","L4-141","3\\8\\34","Ai+","420\\15"]
["PW252-","pH METING AFVOER C-817","QT817B","L4-142","3\\8\\36","Ai-","420\\16"]
["PW254+","pH METING AFVOER C-818","QT818A","L4-143","3\\8\\38","Ai+","420\\17"]
["PW254-","pH METING AFVOER C-818","QT818A","L4-144","3\\8\\40","Ai-","420\\PE"]
[]
[]
[null,"ANALOGE UITGANGEN","REK 3 KAART 14","L4-145","3\\14\\3+24","24VDC","421\\1"]
["PW128-","KLEPSTURING LCV-150 NIVOREG.CONDENSOR",null,"L4-146","3\\14\\6","Ao-","421\\2"]
["PW128+","KLEPSTURING LCV-150 NIVOREG.CONDENSOR",null,"L4-147","3\\14\\7","Ao+","421\\3"]
["PW130-","KLEPSTURING LCV-151 NIVOREG.HOOFDDRUM",null,"L4-148","3\\14\\10","Ao-","421\\4"]
["PW130+","KLEPSTURING LCV-151 NIVOREG.HOOFDDRUM",null,"L4-149","3\\14\\11","Ao+","421\\5"]
["PW132-","KLEPSTURING LCV-152 NIVOREG.NEVENDRUM",null,"L4-150","3\\14\\15","Ao-","421\\6"]
["PW132+","KLEPSTURING LCV-152 NIVOREG.NEVENDRUM",null,"L4-151","3\\14\\16","Ao+","421\\7"]
["PW134-","KLEPSTURING FCV-152 WATERSTR. SECTIE 1","KLEPSTURING FCV-152 WATERSTR. SECTIE 1","L4-152","3\\14\\19","Ao-","421\\8"]
["PW134+","KLEPSTURING FCV-152 WATERSTR. SECTIE 1","KLEPSTURING FCV-152 WATERSTR. SECTIE 1","L4-153","3\\14\\20","Ao+","421\\9"]
[";",";",";","L4-154","3\\14\\21","COM","421\\10"]
["PW136-","KLEPSTURING FCV-153 WATERSTR. SECTIE 2",null,"L4-155","3\\14\\27","Ao-","421\\11"]
["PW136+","KLEPSTURING FCV-153 WATERSTR. SECTIE 2",null,"L4-156","3\\14\\28","Ao+","421\\12"]
["PW138-","KLEPSTURING PCV-162","VUURHAARDDRUKREG. (PCV-162)","L4-157","3\\14\\31","Ao-","421\\13","P162"]
["PW138+","KLEPSTURING PCV-162","VUURHAARDDRUKREG. (PCV-162)","L4-158","3\\14\\32","Ao+","421\\14","P162"]
["PW140-","SPEED MA150","SC-150","L4-159","3\\14\\36","Ao-","421\\15","S-150"]
["PW140+","SPEED MA150","SC-150","L4-160","3\\14\\37","Ao+","421\\16","S-150"]
["PW142-","SPEED MA151","SC-151","L4-161","3\\14\\40","Ao-","421\\17","S-151"]
["PW142+","SPEED MA151","SC-151","L4-162","3\\14\\41","Ao+","421\\PE","S-151"]
[null,"ANALOGE UITGANGEN","REK 3 KAART 15","L4-163","3\\15\\3+24","24VDC","422\\1"]
["PW144-","SPEED MA152","SC-152","L4-164","3\\15\\6","Ao-","422\\2"]
["PW144+","SPEED MA152","SC-152","L4-165","3\\15\\7","Ao+","422\\3"]
["PW146-","SPEED MA153","SC-153","L4-166","3\\15\\10","Ao-","422\\4"]
["PW146+","SPEED MA153","SC-153","L4-167","3\\15\\11","Ao+","422\\5"]
["PW148-","GASTOEVOER HOOFDBRANDERS","TCV184","L4-168","3\\15\\15","Ao-","422\\6"]
["PW148+","GASTOEVOER HOOFDBRANDERS","TCV184","L4-169","3\\15\\16","Ao+","422\\7"]
["PW150-","KOELWATER V190 (TCV910)","KLEPSTURING TCV-182 TEMP. NA LUVO 2","L4-170","3\\15\\19","Ao-","422\\8"]
["PW150+","KOELWATER V190 (TCV910)","KLEPSTURING TCV-182 TEMP. NA LUVO 2","L4-171","3\\15\\20","Ao+","422\\9"]
[";",";",";","L4-172","3\\15\\21","COM","422\\10"]
["PW152-","SPEED MK150  ","SC-154","L4-173","3\\15\\27","Ao-","422\\11","S-154"]
["PW152+","SPEED MK150  ","SC-154","L4-174","3\\15\\28","Ao+","422\\12","S-154"]
["PW154-","SPEED MK158","SC-155","L4-175","3\\15\\31","Ao-","422\\13","S-155"]
["PW154+","SPEED MK158","SC-155","L4-176","3\\15\\32","Ao+","422\\14","S-155"]
["PW156-","XXXXXXXXXX","XXXXXXXXXX","L4-177","3\\15\\36","Ao-","422\\15"]
["PW156+","XXXXXXXXXX","XXXXXXXXXX","L4-178","3\\15\\37","Ao+","422\\16"]
["PW158-","XXXXXXXXXX","XXXXXXXXXX","L4-179","3\\15\\40","Ao-","422\\17"]
["PW158+","XXXXXXXXXX","XXXXXXXXXX","L4-180","3\\15\\41","Ao+","422\\PE"]
[null,"ANALOGE UITGANGEN","REK 3 KAART 16","L4-181","3\\16\\3+24","24VDC","423\\1"]
["PW160+","SPEED MA158",null,"L4-182","3\\16\\6","Ao-","423\\2"]
["PW160-","SPEED MA158",null,"L4-183","3\\16\\7","Ao+","423\\3"]
["PW162+","KLEPSTURING LCV170","LCV170 NIVO REGELING VAT 156          (SEAC)","L4-184","3\\16\\10","Ao-","423\\4","L170"]
["PW162-","KLEPSTURING LCV170","LCV170 NIVO REGELING VAT 156          (SEAC)","L4-185","3\\16\\11","Ao+","423\\5","L170"]
["PW164+","XXXXXXXXXX","XXXXXXXXXX","L4-186","3\\16\\15","Ao-","423\\6"]
["PW164-","XXXXXXXXXX","XXXXXXXXXX","L4-187","3\\16\\16","Ao+","423\\7"]
["PW166+","XXXXXXXXXX","XXXXXXXXXX","L4-188","3\\16\\19","Ao-","423\\8"]
["PW166-","XXXXXXXXXX","XXXXXXXXXX","L4-189","3\\16\\20","Ao+","423\\9"]
[";",";",";","L4-190","3\\16\\21","COM","423\\10"]
["PW168-","KLEPSTURING LCV819-1","LCV819-1   POSTOX.TANK V819 FINALOX.UITL.","L4-191","3\\16\\27","Ao-","423\\11","L819"]
["PW168+","KLEPSTURING LCV819-1","LCV819-1   POSTOX.TANK V819 FINALOX.UITL.","L4-192","3\\16\\28","Ao+","423\\12","L819"]
["PW170-","SPEED A182","SC-182","L4-193","3\\16\\31","Ao-","423\\13"]
["PW170+","SPEED A182","SC-182","L4-194","3\\16\\32","Ao+","423\\14"]
["PW172-","XXXXXXXXXX","XXXXXXXXXX","L4-195","3\\16\\36","Ao-","423\\15"]
["PW172+","XXXXXXXXXX","XXXXXXXXXX","L4-196","3\\16\\37","Ao+","423\\16"]
["PW174-","SETPOINT C-150","TCV170","L4-197","3\\16\\40","Ao-","423\\17"]
["PW174+","SETPOINT C-150","TCV170","L4-198","3\\16\\41","Ao+","423\\PE"]
[null,"ANALOGE UITGANGEN","REK 3 KAART 17","L4-199","3\\17\\3+24","24VDC","424\\1"]
["PW176-",null,"QCV818","L4-200","3\\17\\6","Ao-","424\\2"]
["PW176+",null,"QCV818","L4-201","3\\17\\7","Ao+","424\\3"]
["PW178-",null,"QCV819","L4-202","3\\17\\10","Ao-","424\\4"]
["PW178+",null,"QCV819","L4-203","3\\17\\11","Ao+","424\\5"]
["PW180-","SPEED MA156.2",null,"L4-204","3\\17\\15","Ao-","424\\6"]
["PW180+","SPEED MA156.2",null,"L4-205","3\\17\\16","Ao+","424\\7"]
["PW182-","SPEED MA182",null,"L4-206","3\\17\\19","Ao-","424\\8"]
["PW182+","SPEED MA182",null,"L4-207","3\\17\\20","Ao+","424\\9"]
[";",";",";","L4-208","3\\17\\21","COM","424\\10"]
["PW184-",null,"QCV820-1","L4-209","3\\17\\27","Ao-","424\\11"]
["PW184+",null,"QCV820-1","L4-210","3\\17\\28","Ao+","424\\12"]
["PW186-",null,"QCV820-2","L4-211","3\\17\\31","Ao-","424\\13"]
["PW186+",null,"QCV820-2","L4-212","3\\17\\32","Ao+","424\\14"]
["PW188-","samsonklep","TCV-176","L4-213","3\\17\\36","Ao-","424\\15"]
["PW188+","samsonklep","TCV-176","L4-214","3\\17\\37","Ao+","424\\16"]
["PW190-","XXXXXXXXXX","XXXXXXXXXX","L4-215","3\\17\\40","Ao-","424\\17"]
["PW190+","XXXXXXXXXX","XXXXXXXXXX","L4-216","3\\17\\41","Ao+","424\\PE"]
[null,null,"REK 3 KAART 18","L4-409","3\\18\\3+24","24VDC","425\\1"]
["PW192-",null,null,"L4-410","3\\18\\6","Ao-","425\\2"]
["PW192+",null,null,"L4-411","3\\18\\7","Ao+","425\\3"]
["PW194-",null,null,"L4-412","3\\18\\10","Ao-","425\\4"]
["PW194+",null,null,"L4-413","3\\18\\11","Ao+","425\\5"]
["PW196-","TIC-147 tempreg. Doekenfilter","TIC-147","L4-414","3\\18\\15","Ao-","425\\6"]
["PW196+","TIC-147","TIC-147","L4-415","3\\18\\16","Ao+","425\\7"]
["PW198-","PIC-812","PIC-812","L4-416","3\\18\\19","Ao-","425\\8"]
["PW198+","PIC-812","PIC-812","L4-417","3\\18\\20","Ao+","425\\9"]
[null,null,null,"L4-418","3\\18\\27","Ao-","425\\10"]
["PW200-","SIC-153","SIC-153","L4-419","3\\18\\28","Ao+","425\\11"]
["PW200+","SIC-153","SIC-153","L4-420","3\\18\\31","Ao-","425\\12"]
[null,null,null,"L4-421","3\\18\\32","Ao+","425\\13"]
[null,null,null,"L4-422","3\\18\\36","Ao-","425\\14"]
[null,null,null,"L4-423","3\\18\\37","Ao+","425\\15"]
[null,null,null,"L4-424","3\\18\\40","Ao-","425\\16"]
[null,null,null,"L4-425","3\\18\\41","Ao+","425\\17"]
[null,null,null,"L4-426","3\\18\\21","COM","425\\18"]
[null,null,null,"L4-427","3\\18\\42","GND","425\\19"]
[null,null,null,"L4-428","Vent.",null,"425\\20"]
[null,null,null,"L4-429","Vent.",null,"425\\21"]
[null,"ANALOGE INGANGEN 16 KAARTEN REK 1"]
[null,null,null,"HLRVD","R/K/Aans","FUNCTIE","KABEL/NR"]
[null,"OUDE VERWIJZING","NIEUWE VERWIJZING"]
[";","ANALOGE INGANGEN","REK 1 KAART 1","L4-217","1\\1\\3+24","24VDC","377\\1"]
["QW0+","TRANSP.SCHROEF A-158","FT-170","L4-218","1\\1\\4","Ai+","377\\2"]
["QW0-","TRANSP.SCHROEF A-158","FT-170","L4-219","1\\1\\6","Ai-","377\\3"]
["QW2+","TRANSP.SCHROEF A-182","ST182","L4-220","1\\1\\8","Ai+","377\\4"]
["QW2-","TRANSP.SCHROEF A-182","ST182","L4-221","1\\1\\10","Ai-","377\\5"]
["QW4+","PRODUCT TANK V-800B","LT800-4","L4-222","1\\1\\13","Ai+","377\\6"]
["QW4-","PRODUCT TANK V-800B","LT800-4","L4-223","1\\1\\15","Ai-","377\\7"]
["QW6+","DRUK DOEKENFILTER ","PT918","L4-224","1\\1\\17","Ai+","377\\8"]
["QW6-","DRUK DOEKENFILTER ","PT918","L4-225","1\\1\\19","Ai-","377\\9"]
[";",";",";","L4-226","1\\1\\21","COM","377\\10"]
["QW8+","NIVO VAT 950 (LT 913)","LT913","L4-227","1\\1\\25","Ai+","377\\11"]
["QW8-","NIVO VAT 950 (LT 913)","LT913","L4-228","1\\1\\27","Ai-","377\\12"]
["QW10+","TEMP. BED 1","TT158-1","L4-229","1\\1\\29","Ai+","377\\13"]
["QW10-","TEMP. BED 1","TT158-1","L4-230","1\\1\\31","Ai-","377\\14"]
["QW12+","TEMP. BED 2","TT159-1","L4-231","1\\1\\34","Ai+","377\\15"]
["QW12-","TEMP. BED 2","TT159-1","L4-232","1\\1\\36","Ai-","377\\16"]
["QW14+","WERKLUCHTDRUK COMPRESSOR V172","PT919","L4-233","1\\1\\38","Ai+","377\\17"]
["QW14-","WERKLUCHTDRUK COMPRESSOR V172","PT919","L4-234","1\\1\\40","Ai-","377\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 2","L4-235","1\\2\\3+24","24VDC","378\\1"]
["QW16+","NIVO BUFFERVAT V316","LI316","L4-236","1\\2\\4","Ai+","378\\2"]
["QW16-","NIVO BUFFERVAT V316","LI316","L4-237","1\\2\\6","Ai-","378\\3"]
["QW18+","FLOW VAN V316 NAAR V310","LT-815.1 niveaumeting quench","L4-238","1\\2\\8","Ai+","378\\4"]
["QW18-","FLOW VAN V316 NAAR V310","LT-815.1 niveaumeting quench","L4-239","1\\2\\10","Ai-","378\\5"]
["QW20+","FLOW VAN V317 NAAR V312","terugkoppeling frequetieomvormer K-151.2","L4-240","1\\2\\13","Ai+","378\\6"]
["QW20-","FLOW VAN V317 NAAR V312","terugkoppeling frequetieomvormer K-151.2","L4-241","1\\2\\15","Ai-","378\\7"]
["QW22+","Mo03 CONCENTRATIE","terugkoppeling frequetieomvormer K-818.1","L4-242","1\\2\\17","Ai+","378\\8"]
["QW22-","Mo03 CONCENTRATIE","terugkoppeling frequetieomvormer K-818.1","L4-243","1\\2\\19","Ai-","378\\9"]
[";",";",";","L4-244","1\\2\\21","COM","378\\10"]
["QW24+","NIVO IN VAT 318","LI318","L4-245","1\\2\\25","Ai+","378\\11"]
["QW24-","NIVO IN VAT 318","LI318","L4-246","1\\2\\27","Ai-","378\\12"]
["QW26+","FLOW SCRUBVL. NAAR V313","FI313","L4-247","1\\2\\29","Ai+","378\\13"]
["QW26-","FLOW SCRUBVL. NAAR V313","FI313","L4-248","1\\2\\31","Ai-","378\\14"]
["QW28+","pH SCRUBSTAB","pHI313","L4-249","1\\2\\34","Ai+","378\\15"]
["QW28-","pH SCRUBSTAB","pHI313","L4-250","1\\2\\36","Ai-","378\\16"]
["QW30+","NIVO BUFFERVAT V320","LI320","L4-251","1\\2\\38","Ai+","378\\17"]
["QW30-","NIVO BUFFERVAT V320","LI320","L4-252","1\\2\\40","Ai-","378\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 3","L4-253","1\\3\\3+24","24VDC","379\\1"]
["QW32+","FLOW AM.PARAM. V314","FI319","L4-254","1\\3\\4","Ai+","379\\2"]
["QW32-","FLOW AM.PARAM. V314","FI319","L4-255","1\\3\\6","Ai-","379\\3"]
["QW34+","pH VAT 314","pHI314","L4-256","1\\3\\8","Ai+","379\\4"]
["QW34-","pH VAT 314","pHI314","L4-257","1\\3\\10","Ai-","379\\5"]
["QW36+","NIVO VAT 319","LI319","L4-258","1\\3\\13","Ai+","379\\6"]
["QW36-","NIVO VAT 319","LI319","L4-259","1\\3\\15","Ai-","379\\7"]
["QW38+","NIVO VAT 321","LI321","L4-260","1\\3\\17","Ai+","379\\8"]
["QW38-","NIVO VAT 321","LI321","L4-261","1\\3\\19","Ai-","379\\9"]
[";",";",";","L4-262","1\\3\\21","COM","379\\10"]
["QW40+","VERBR.LUCHTSTR.REG.Bed 1 (FT-198)","FT-158","L4-263","1\\3\\25","Ai+","379\\11"]
["QW40-","VERBR.LUCHTSTR.REG.Bed 1 (FT-198)","FT-158","L4-264","1\\3\\27","Ai-","379\\12"]
["QW42+","VERBR.LUCHTSTR.REG.Bed 2 (FT-199)","FT-159","L4-265","1\\3\\29","Ai+","379\\13"]
["QW42-","VERBR.LUCHTSTR.REG.Bed 2 (FT-199)","FT-159","L4-266","1\\3\\31","Ai-","379\\14"]
["QW44+","XXXXXXXXXX","XXXXXXXXXX","L4-267","1\\3\\34","Ai+","379\\15"]
["QW44-","XXXXXXXXXX","XXXXXXXXXX","L4-268","1\\3\\36","Ai-","379\\16"]
["QW46+","XXXXXXXXXX","XXXXXXXXXX","L4-269","1\\3\\38","Ai+","379\\17"]
["QW46-","XXXXXXXXXX","XXXXXXXXXX","L4-270","1\\3\\40","Ai-","379\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 4","L4-271","1\\4\\3+24","24VDC","380\\1"]
["QW48+","TE-804 temperatuur V-804","TE-804 temperatuur in V-804","L4-272","1\\4\\4","Ai+","380\\2"]
["QW48-","TE-804 temperatuur V-804","TE-804 temperatuur in V-804","L4-273","1\\4\\6","Ai-","380\\3"]
["QW50+","TE-804 temperatuur V-804","TE-804 temperatuur in V-804","L4-274","1\\4\\8","Ai+","380\\4"]
["QW50-","TE-804 temperatuur V-804","TE-804 temperatuur in V-804","L4-275","1\\4\\10","Ai-","380\\5"]
["QW52+","temperatuur uitlaat quench","TE-813 uitgangstemperatuur quench","L4-276","1\\4\\13","Ai+","380\\6"]
["QW52-","temperatuur uitlaat quench","TE-813 uitgangstemperatuur quench","L4-277","1\\4\\15","Ai-","380\\7"]
["QW54+","temperatuur uitlaat quench","TE-813 uitgangstemperatuur quench","L4-278","1\\4\\17","Ai+","380\\8"]
["QW54-","temperatuur uitlaat quench","TE-813 uitgangstemperatuur quench","L4-279","1\\4\\19","Ai-","380\\9"]
[";",";",";","L4-280","1\\4\\21","COM","380\\10"]
["QW56+","Temperatuur koelwaterbak V-910","TIC-910 temperatuur koelwater V-910","L4-281","1\\4\\25","Ai+","380\\11"]
["QW56-","Temperatuur koelwaterbak V-910","TIC-910 temperatuur koelwater V-910","L4-282","1\\4\\27","Ai-","380\\12"]
["QW58+","Temperatuur koelwaterbak V-910","TIC-910 temperatuur koelwater V-910","L4-283","1\\4\\29","Ai+","380\\13"]
["QW58-","Temperatuur koelwaterbak V-910","TIC-910 temperatuur koelwater V-910","L4-284","1\\4\\31","Ai-","380\\14"]
["QW60+","XXXXXXXXXX","XXXXXXXXXX","L4-285","1\\4\\34","Ai+","380\\15"]
["QW60-","XXXXXXXXXX","XXXXXXXXXX","L4-286","1\\4\\36","Ai-","380\\16"]
["QW62+","XXXXXXXXXX","XXXXXXXXXX","L4-287","1\\4\\38","Ai+","380\\17"]
["QW62-","XXXXXXXXXX","XXXXXXXXXX","L4-288","1\\4\\40","Ai-","380\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 5","L4-289","1\\5\\3+24","24VDC","381\\1"]
["QW64+","pH 1e WASKOLOM C816","pHI816","L4-290","1\\5\\4","Ai+","381\\2"]
["QW64-","pH 1e WASKOLOM C816","pHI816","L4-291","1\\5\\6","Ai-","381\\3"]
["QW66+","pH 2e WASKOLOM C817","pHI817","L4-292","1\\5\\8","Ai+","381\\4"]
["QW66-","pH 2e WASKOLOM C817","pHI817","L4-293","1\\5\\10","Ai-","381\\5"]
["QW68+","pH 3e WASKOLOM C818","pHI818","L4-294","1\\5\\13","Ai+","381\\6"]
["QW68-","pH 3e WASKOLOM C818","pHI818","L4-295","1\\5\\15","Ai-","381\\7"]
["QW70+","pH OXIDATIEVAT V819","pHI819","L4-296","1\\5\\17","Ai+","381\\8"]
["QW70-","pH OXIDATIEVAT V819","pHI819","L4-297","1\\5\\19","Ai-","381\\9"]
[";",";",";","L4-298","1\\5\\21","COM","381\\10"]
["QW72+","SO2 CONCENT. IN ROOKGAS","QI818","L4-299","1\\5\\25","Ai+","381\\11"]
["QW72-","SO2 CONCENT. IN ROOKGAS","QI818","L4-300","1\\5\\27","Ai-","381\\12"]
["QW74+","FLOW NAAR VAT 819","FT820","L4-301","1\\5\\29","Ai+","381\\13"]
["QW74-","FLOW NAAR VAT 819","FT820","L4-302","1\\5\\31","Ai-","381\\14"]
["QW76+","NIVO C818","LT818","L4-303","1\\5\\34","Ai+","381\\15"]
["QW76-","NIVO C818","LT818","L4-304","1\\5\\36","Ai-","381\\16"]
["QW78+","NIVO VAT 819","LT821","L4-305","1\\5\\38","Ai+","381\\17"]
["QW78-","NIVO VAT 819","LT821","L4-306","1\\5\\40","Ai-","381\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 6","L4-307","1\\6\\3+24","24VDC","382\\1"]
["QW80+","WERKLUCHTDRUK COMPRESSOR MK172","PT-191","L4-308","1\\6\\4","Ai+","382\\2"]
["QW80-","WERKLUCHTDRUK COMPRESSOR MK172","PT-191","L4-309","1\\6\\6","Ai-","382\\3"]
["QW82+","Inlaat temparatuur sproeikoeler","TE171","L4-310","1\\6\\8","Ai+","382\\4"]
["QW82-","Inlaat temparatuur sproeikoeler","TE171","L4-311","1\\6\\10","Ai-","382\\5"]
["QW84+","O2 meter FBO","QT-150","L4-312","1\\6\\13","Ai+","382\\6"]
["QW84-","O2 meter FBO","QT-150","L4-313","1\\6\\15","Ai-","382\\7"]
["QW86+","Uitlaat temperatuur sproeikoeler","TE172","L4-314","1\\6\\17","Ai+","382\\8"]
["QW86-","Uitlaat temperatuur sproeikoeler","TE172","L4-315","1\\6\\19","Ai-","382\\9"]
[";",";",";","L4-316","1\\6\\21","COM","382\\10"]
["QW88+","WATERFLOW NAAR C-150 (BRANDERS)","FT170","L4-317","1\\6\\25","Ai+","382\\11"]
["QW88-","WATERFLOW NAAR C-150 (BRANDERS)","FT170","L4-318","1\\6\\27","Ai-","382\\12"]
["QW90+","NIVO VAT 156 (LT172)","LT171-1","L4-319","1\\6\\29","Ai+","382\\13"]
["QW90-","NIVO VAT 156 (LT172)","LT171-1","L4-320","1\\6\\31","Ai-","382\\14"]
["QW92+","NIVO VAT 970 (LT970)","XXXXXXXXXX","L4-321","1\\6\\34","Ai+","382\\15"]
["QW92-","NIVO VAT 970 (LT970)","XXXXXXXXXX","L4-322","1\\6\\36","Ai-","382\\16"]
["QW94+","DRUK VAT 970  (PT970) (BRANDERS)","XXXXXXXXXX","L4-323","1\\6\\38","Ai+","382\\17"]
["QW94-","DRUK VAT 970  (PT970) (BRANDERS)","XXXXXXXXXX","L4-324","1\\6\\40","Ai-","382\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 7","L4-325","1\\7\\3+24","24VDC","383\\1"]
["QW96+","INJECTIETEMPERATUUR (TE1002)","TE1002","L4-326","1\\7\\4","Ai+","383\\2"]
["QW96-","INJECTIETEMPERATUUR (TE1002)","TE1002","L4-327","1\\7\\6","Ai-","383\\3"]
["QW98+","XXXXXXXXXX","XXXXXXXXXX","L4-328","1\\7\\8","Ai+","383\\4"]
["QW98-","XXXXXXXXXX","XXXXXXXXXX","L4-329","1\\7\\10","Ai-","383\\5"]
["QW100+","XXXXXXXXXX","XXXXXXXXXX","L4-330","1\\7\\13","Ai+","383\\6"]
["QW100-","XXXXXXXXXX","XXXXXXXXXX","L4-331","1\\7\\15","Ai-","383\\7"]
["QW102+","XXXXXXXXXX","XXXXXXXXXX","L4-332","1\\7\\17","Ai+","383\\8"]
["QW102-","XXXXXXXXXX","XXXXXXXXXX","L4-333","1\\7\\19","Ai-","383\\9"]
[";",";",";","L4-334","1\\7\\21","COM","383\\10"]
["QW104+","XXXXXXXXXX","XXXXXXXXXX","L4-335","1\\7\\25","Ai+","383\\11"]
["QW104-","XXXXXXXXXX","XXXXXXXXXX","L4-336","1\\7\\27","Ai-","383\\12"]
["QW106+","XXXXXXXXXX","XXXXXXXXXX","L4-337","1\\7\\29","Ai+","383\\13"]
["QW106-","XXXXXXXXXX","XXXXXXXXXX","L4-338","1\\7\\31","Ai-","383\\14"]
["QW108+","XXXXXXXXXX","XXXXXXXXXX","L4-339","1\\7\\34","Ai+","383\\15"]
["QW108-","XXXXXXXXXX","XXXXXXXXXX","L4-340","1\\7\\36","Ai-","383\\16"]
["QW110+","Terugkoppeling frequentieomvormer K-151.1","Terugkoppeling frequentieomvormer K-151.1","L4-341","1\\7\\38","Ai+","383\\17"]
["QW110-","Terugkoppeling frequentieomvormer K-151.1","Terugkoppeling frequentieomvormer K-151.1","L4-342","1\\7\\40","Ai-","383\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 8","L4-343","1\\8\\3+24","24VDC","384\\1"]
["QW112+","TEMP.BED 2","TE161-1","L4-344","1\\8\\4","Ai+","384\\2"]
["QW112-","TEMP.BED 2","TE161-1","L4-345","1\\8\\6","Ai-","384\\3"]
["QW114+","TEMPERATUUR UITGANG QUENCH","TI815","L4-346","1\\8\\8","Ai+","384\\4"]
["QW114-","TEMPERATUUR UITGANG QUENCH","TI815","L4-347","1\\8\\10","Ai-","384\\5"]
["QW116+","XXXXXXXXXX","XXXXXXXXXX","L4-348","1\\8\\13","Ai+","384\\6"]
["QW116-","XXXXXXXXXX","XXXXXXXXXX","L4-349","1\\8\\15","Ai-","384\\7"]
["QW118+","XXXXXXXXXX","XXXXXXXXXX","L4-350","1\\8\\17","Ai+","384\\8"]
["QW118-","XXXXXXXXXX","XXXXXXXXXX","L4-351","1\\8\\19","Ai-","384\\9"]
[";",";",";","L4-352","1\\8\\21","COM","384\\10"]
["QW120+","XXXXXXXXXX","XXXXXXXXXX","L4-353","1\\8\\25","Ai+","384\\11"]
["QW120-","XXXXXXXXXX","XXXXXXXXXX","L4-354","1\\8\\27","Ai-","384\\12"]
["QW122+","XXXXXXXXXX","Frequentie aan","L4-355","1\\8\\29","Ai+","384\\13"]
["QW122-","XXXXXXXXXX","XXXXXXXXXX","L4-356","1\\8\\31","Ai-","384\\14"]
["QW124+","XXXXXXXXXX","XXXXXXXXXX","L4-357","1\\8\\34","Ai+","384\\15"]
["QW124-","XXXXXXXXXX","XXXXXXXXXX","L4-358","1\\8\\36","Ai-","384\\16"]
["QW126+","XXXXXXXXXX","XXXXXXXXXX","L4-359","1\\8\\38","Ai+","384\\17"]
["QW126-","XXXXXXXXXX","XXXXXXXXXX","L4-360","1\\8\\40","Ai-","384\\PE"]
[null,null,null,"LL-RVD"]
[";","ANALOGE INGANGEN","REK 1 KAART 9","L2-1","1\\9\\3+24","24VDC","385\\1"]
["QW128+","TEMPERATUUR INLAAT KETEL","TE150","L2-2","1\\9\\4","Ai+","385\\2"]
["QW128-","TEMPERATUUR INLAAT KETEL","TE150","L2-3","1\\9\\6","Ai-","385\\3"]
["QW130+","TEMPERATUUR STOOM SECTIE 1","TE151","L2-4","1\\9\\8","Ai+","385\\4"]
["QW130-","TEMPERATUUR STOOM SECTIE 1","TE151","L2-5","1\\9\\10","Ai-","385\\5"]
["QW132+","TEMPERATUUR STOOM SECTIE 2","TE152","L2-6","1\\9\\13","Ai+","385\\6"]
["QW132-","TEMPERATUUR STOOM SECTIE 2","TE152","L2-7","1\\9\\15","Ai-","385\\7"]
["QW134+","TEMPERATUUR UITLAAT WERVELBED","TE160-1","L2-8","1\\9\\17","Ai+","385\\8"]
["QW134-","TEMPERATUUR UITLAAT WERVELBED","TE160-1","L2-9","1\\9\\19","Ai-","385\\9"]
[";",";",";","L2-10","1\\9\\21","COM","385\\10"]
["QW136+","TEMPERATUUR UITLAAT MEMBRAANWANDEN","TE154","L2-11","1\\9\\25","Ai+","385\\11"]
["QW136-","TEMPERATUUR UITLAAT MEMBRAANWANDEN","TE154","L2-12","1\\9\\27","Ai-","385\\12"]
["QW138+","TEMPERATUUR BED 1","TE158-2","L2-13","1\\9\\29","Ai+","385\\13"]
["QW138-","TEMPERATUUR BED 1","TE158-2","L2-14","1\\9\\31","Ai-","385\\14"]
["QW140+","TEMPERATUUR BED 1","TE158-3","L2-15","1\\9\\34","Ai+","385\\15"]
["QW140-","TEMPERATUUR BED 1","TE158-3","L2-16","1\\9\\36","Ai-","385\\16"]
["QW142+","TEMPERATUUR BED 1","TE160-2","L2-17","1\\9\\38","Ai+","385\\17"]
["QW142-","TEMPERATUUR BED 1","TE160-2","L2-18","1\\9\\40","Ai-","385\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 10","L2-19","1\\10\\3+24","24VDC","386\\1"]
["QW144","TEMP.BED 2","TE159-2","L2-20","1\\10\\4","Ai+","386\\2"]
["QW144-","TEMP.BED 2","TE159-2","L2-21","1\\10\\6","Ai-","386\\3"]
["QW146+","TEMP.BED 2","TE159-3","L2-22","1\\10\\8","Ai+","386\\4"]
["QW146-","TEMP.BED 2","TE159-3","L2-23","1\\10\\10","Ai-","386\\5"]
["QW148+","TEMP.BED 2","TE161-2","L2-24","1\\10\\13","Ai+","386\\6"]
["QW148-","TEMP.BED 2","TE161-2","L2-25","1\\10\\15","Ai-","386\\7"]
["QW150+","TEMP.VOOR 1e CONVECTOR","TE162-1","L2-26","1\\10\\17","Ai+","386\\8"]
["QW150-","TEMP.VOOR 1e CONVECTOR","TE162-1","L2-27","1\\10\\19","Ai-","386\\9"]
[";",";",";","L2-28","1\\10\\21","COM","386\\10"]
["QW152+","TEMP.VOOR 1e CONVECTOR","TE188","L2-29","1\\10\\25","Ai+","386\\11"]
["QW152-","TEMP.VOOR 1e CONVECTOR","TE162-2","L2-30","1\\10\\27","Ai-","386\\12"]
["QW154+","TEMP.VOOR 1e CONVECTOR","TE163-1","L2-31","1\\10\\29","Ai+","386\\13"]
["QW154-","TEMP.VOOR 1e CONVECTOR","TE163-1","L2-32","1\\10\\31","Ai-","386\\14"]
["QW156+","TEMP.ROOKGASKETEL","TE164","L2-33","1\\10\\34","Ai+","386\\15"]
["QW156-","TEMP.ROOKGASKETEL","TE164","L2-34","1\\10\\36","Ai-","386\\16"]
["QW158+","TEMP.BOVEN IN KETEL","TE165 ","L2-35","1\\10\\38","Ai+","386\\17"]
["QW158-","TEMP.BOVEN IN KETEL","TE165 ","L2-36","1\\10\\40","Ai-","386\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 11","L2-37","1\\11\\3+24","24VDC","387\\1"]
["QW160+","BUITENLUCHTTEMP.INLAAT VERBR.VENT.","TE167","L2-38","1\\11\\4","Ai+","387\\2"]
["QW160-","BUITENLUCHTTEMP.INLAAT VERBR.VENT.","TE167","L2-39","1\\11\\6","Ai-","387\\3"]
["QW162+","TEMP.LUCHT NAAR LUVO'S","TE168","L2-40","1\\11\\8","Ai+","387\\4"]
["QW162-","TEMP.LUCHT NAAR LUVO'S","TE168","L2-41","1\\11\\10","Ai-","387\\5"]
["QW164+","TEMP.PNEUM.TRANSP.BED 1","TE169","L2-42","1\\11\\13","Ai+","387\\6"]
["QW164-","TEMP.PNEUM.TRANSP.BED 1","TE169","L2-43","1\\11\\15","Ai-","387\\7"]
["QW166+","TEMP.PNEUM.TRANSP.BED 2","TE170","L2-44","1\\11\\17","Ai+","387\\8"]
["QW166-","TEMP.PNEUM.TRANSP.BED 2","TE170","L2-45","1\\11\\19","Ai-","387\\9"]
[";",";",";","L2-46","1\\11\\21","COM","387\\10"]
["QW168+","TEMP.PNEUM.TRANSP.BREKER","TE171","L2-47","1\\11\\25","Ai+","387\\11"]
["QW168-","TEMP.PNEUM.TRANSP.BREKER","TE171","L2-48","1\\11\\27","Ai-","387\\12"]
["QW170+","TEMP. NA ASKOELER","TE175","L2-49","1\\11\\29","Ai+","387\\13"]
["QW170-","TEMP. NA ASKOELER","TE175","L2-50","1\\11\\31","Ai-","387\\14"]
["QW172+","TEMP. NA LUVO 1","TE181-1","L2-51","1\\11\\34","Ai+","387\\15"]
["QW172-","TEMP. NA LUVO 1","TE181-1","L2-52","1\\11\\36","Ai-","387\\16"]
["QW174+","TEMP. NA LUVO 2 (TE182-1)","TE804","L2-53","1\\11\\38","Ai+","387\\17"]
["QW174-","TEMP. NA LUVO 2 (TE182-1)","TE804","L2-54","1\\11\\40","Ai-","387\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 12","L2-55","1\\12\\3+24","24VDC","388\\1"]
["QW176+","TEMP. KAT. BUNKER 1","TE186","L2-56","1\\12\\4","Ai+","388\\2"]
["QW176-","TEMP. KAT. BUNKER 1","TE186","L2-57","1\\12\\6","Ai-","388\\3"]
["QW178+","TEMP. KAT. BUNKER 2","TE187","L2-58","1\\12\\8","Ai+","388\\4"]
["QW178-","TEMP. KAT. BUNKER 2","TE187","L2-59","1\\12\\10","Ai-","388\\5"]
["QW180+","TEMP. KAT. BUNKER 3&4","TE188","L2-60","1\\12\\13","Ai+","388\\6"]
["QW180-","TEMP. KAT. BUNKER 3&4","TE188","L2-61","1\\12\\15","Ai-","388\\7"]
["QW182+","TEMP. FILTER AFZUIGINSTALLATIE","TE189","L2-62","1\\12\\17","Ai+","388\\8"]
["QW182-","TEMP. FILTER AFZUIGINSTALLATIE","TE189","L2-63","1\\12\\19","Ai-","388\\9"]
[";",";",";","L2-64","1\\12\\21","COM","388\\10"]
["QW184+","ROOKGASTEMP.UITLAAT C-815","TE813","L2-65","1\\12\\25","Ai+","388\\11"]
["QW184-","ROOKGASTEMP.UITLAAT C-815","TE813","L2-66","1\\12\\27","Ai-","388\\12"]
["QW186+","Temp. Samsonklep","TE176","L2-67","1\\12\\29","Ai+","388\\13"]
["QW186-","Temp. Samsonklep","TE176","L2-68","1\\12\\31","Ai-","388\\14"]
["QW188+","TEMP. BUNKER B154","TE190","L2-69","1\\12\\34","Ai+","388\\15"]
["QW188-","TEMP. BUNKER B154","TE190","L2-70","1\\12\\36","Ai-","388\\16"]
["QW190+","TEMP. BUNKER B155","TE191","L2-71","1\\12\\38","Ai+","388\\17"]
["QW190-","TEMP. BUNKER B155","TE191","L2-72","1\\12\\40","Ai-","388\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 13","L2-73","1\\13\\3+24","24VDC","389\\1"]
["QW192+","TEMP.KATBUNKER B150","TE192","L2-74","1\\13\\4","Ai+","389\\2"]
["QW192-","TEMP.KATBUNKER B150","TE192","L2-75","1\\13\\6","Ai-","389\\3"]
["QW194+","TEMP.KATBUNKER B150","TE193","L2-76","1\\13\\8","Ai+","389\\4"]
["QW194-","TEMP.KATBUNKER B150","TE193","L2-77","1\\13\\10","Ai-","389\\5"]
["QW196+","TEMP.KATBUNKER B151","TE194","L2-78","1\\13\\13","Ai+","389\\6"]
["QW196-","TEMP.KATBUNKER B151","TE194","L2-79","1\\13\\15","Ai-","389\\7"]
["QW198+","TEMP.KATBUNKER B151","TE195","L2-80","1\\13\\17","Ai+","389\\8"]
["QW198-","TEMP.KATBUNKER B151","TE195","L2-81","1\\13\\19","Ai-","389\\9"]
[";",";",";","L2-82","1\\13\\21","COM","389\\10"]
["QW200+","TEMP.KOELWATER V910","TE910","L2-83","1\\13\\25","Ai+","389\\11"]
["QW200-","TEMP.KOELWATER V910","TE910","L2-84","1\\13\\27","Ai-","389\\12"]
["QW202+","TEMP. D150","TE165-2","L2-85","1\\13\\29","Ai+","389\\13"]
["QW202-","TEMP. D150","TE165-2","L2-86","1\\13\\31","Ai-","389\\14"]
["QW204+","XXXXXXXXXX","XXXXXXXXXX","L2-87","1\\13\\34","Ai+","389\\15"]
["QW204-","XXXXXXXXXX","XXXXXXXXXX","L2-88","1\\13\\36","Ai-","389\\16"]
["QW206+","XXXXXXXXXX","XXXXXXXXXX","L2-89","1\\13\\38","Ai+","389\\17"]
["QW206-","XXXXXXXXXX","XXXXXXXXXX","L2-90","1\\13\\40","Ai-","389\\PE"]
[";","ANALOGE INGANGEN","REK 1 KAART 14","L2-91","1\\14\\3+24","24VDC","390\\1"]
["QW208+","XXXXXXXXXX","XXXXXXXXXX","L2-92","1\\14\\4","Ai+","390\\2"]
["QW208-","XXXXXXXXXX","XXXXXXXXXX","L2-93","1\\14\\6","Ai-","390\\3"]
["QW210+","XXXXXXXXXX","XXXXXXXXXX","L2-94","1\\14\\8","Ai+","390\\4"]
["QW210-","XXXXXXXXXX","XXXXXXXXXX","L2-95","1\\14\\10","Ai-","390\\5"]
["QW212+","XXXXXXXXXX","XXXXXXXXXX","L2-96","1\\14\\13","Ai+","390\\6"]
["QW212-","XXXXXXXXXX","XXXXXXXXXX","L2-97","1\\14\\15","Ai-","390\\7"]
["QW214+","XXXXXXXXXX","XXXXXXXXXX","L2-98","1\\14\\17","Ai+","390\\8"]
["QW214-","XXXXXXXXXX","XXXXXXXXXX","L2-99","1\\14\\19","Ai-","390\\9"]
[";",";",";","L2-100","1\\14\\21","COM","390\\10"]
["QW216+","XXXXXXXXXX","XXXXXXXXXX","L2-101","1\\14\\25","Ai+","390\\11"]
["QW216-","XXXXXXXXXX","XXXXXXXXXX","L2-102","1\\14\\27","Ai-","390\\12"]
["QW218+","XXXXXXXXXX","XXXXXXXXXX","L2-103","1\\14\\29","Ai+","390\\13"]
["QW218-","XXXXXXXXXX","XXXXXXXXXX","L2-104","1\\14\\31","Ai-","390\\14"]
["QW220+","XXXXXXXXXX","XXXXXXXXXX","L2-105","1\\14\\34","Ai+","390\\15"]
["QW220-","XXXXXXXXXX","XXXXXXXXXX","L2-106","1\\14\\36","Ai-","390\\16"]
["QW222+","XXXXXXXXXX","XXXXXXXXXX","L2-107","1\\14\\38","Ai+","390\\17"]
["QW222_","XXXXXXXXXX","XXXXXXXXXX","L2-108","1\\14\\40","Ai-","390\\PE"]
[null,"ANALOGE INGANGEN","REK 1 KAART 15","L2-109","1\\15\\3+24","24VDC","391\\1"]
["QW224+","XXXXXXXXXX","XXXXXXXXXX","L2-110","1\\15\\4","Ai+","391\\2"]
["QW224-","XXXXXXXXXX","XXXXXXXXXX","L2-111","1\\15\\6","Ai-","391\\3"]
["QW226+","XXXXXXXXXX","XXXXXXXXXX","L2-112","1\\15\\8","Ai+","391\\4"]
["QW226-","XXXXXXXXXX","XXXXXXXXXX","L2-113","1\\15\\10","Ai-","391\\5"]
["QW228+","XXXXXXXXXX","XXXXXXXXXX","L2-114","1\\15\\13","Ai+","391\\6"]
["QW228-","XXXXXXXXXX","XXXXXXXXXX","L2-115","1\\15\\15","Ai-","391\\7"]
["QW230+","XXXXXXXXXX","XXXXXXXXXX","L2-116","1\\15\\17","Ai+","391\\8"]
["QW230-","XXXXXXXXXX","XXXXXXXXXX","L2-117","1\\15\\19","Ai-","391\\9"]
[";",";",";","L2-118","1\\15\\21","COM","391\\10"]
["QW232+","XXXXXXXXXX","XXXXXXXXXX","L2-119","1\\15\\25","Ai+","391\\11"]
["QW232-","XXXXXXXXXX","XXXXXXXXXX","L2-120","1\\15\\27","Ai-","391\\12"]
["QW234+","XXXXXXXXXX","XXXXXXXXXX","L2-121","1\\15\\29","Ai+","391\\13"]
["QW234-","XXXXXXXXXX","XXXXXXXXXX","L2-122","1\\15\\31","Ai-","391\\14"]
["QW236+","XXXXXXXXXX","XXXXXXXXXX","L2-123","1\\15\\34","Ai+","391\\15"]
["QW236-","XXXXXXXXXX","XXXXXXXXXX","L2-124","1\\15\\36","Ai-","391\\16"]
["QW238+","XXXXXXXXXX","XXXXXXXXXX","L2-125","1\\15\\38","Ai+","391\\17"]
["QW238-","XXXXXXXXXX","XXXXXXXXXX","L2-126","1\\15\\40","Ai-","391\\PE"]
[null,"ANALOGE INGANGEN","REK 1 KAART 16","L2-127","1\\16\\3+24","24VDC","392\\1"]
["QW240+","XXXXXXXXXX","XXXXXXXXXX","L2-128",null,null,"392\\2"]
["QW240-","XXXXXXXXXX","XXXXXXXXXX","L2-129",null,null,"392\\3"]
["QW242+","XXXXXXXXXX","XXXXXXXXXX","L2-130",null,null,"392\\4"]
["QW242-","XXXXXXXXXX","XXXXXXXXXX","L2-131",null,null,"392\\5"]
["QW244+","XXXXXXXXXX","XXXXXXXXXX","L2-132",null,null,"392\\6"]
["QW244-","XXXXXXXXXX","XXXXXXXXXX","L2-133",null,null,"392\\7"]
["QW246+","XXXXXXXXXX","XXXXXXXXXX","L2-134",null,null,"392\\8"]
["QW246-","XXXXXXXXXX","XXXXXXXXXX","L2-135",null,null,"392\\9"]
[";",";",";","L2-136",null,"COM","392\\10"]
["QW250+","XXXXXXXXXX","XXXXXXXXXX","L2-137",null,null,"392\\11"]
["QW250-","XXXXXXXXXX","XXXXXXXXXX","L2-138",null,null,"392\\12"]
["QW252+","XXXXXXXXXX","XXXXXXXXXX","L2-139",null,null,"392\\13"]
["QW252-","XXXXXXXXXX","XXXXXXXXXX","L2-140",null,null,"392\\14"]
["QW254+","XXXXXXXXXX","XXXXXXXXXX","L2-141",null,null,"392\\15"]
["QW254-","XXXXXXXXXX","XXXXXXXXXX","L2-142",null,null,"392\\16"]
["QW256+","XXXXXXXXXX","XXXXXXXXXX","L2-143",null,null,"392\\17"]
["QW256-","XXXXXXXXXX","XXXXXXXXXX","L2-144",null,null,"392\\PE"]
[null,"1300 RANGEERKLEMMEN"]
[]
[]
[null,"GEBRUIKTE MEMORYBITS"]
[";",";",";"]
["M 0.0 ","ON LOGISCHE \"1\" ","ON LOGISCHE \"1\" "]
["M 0.1","OFF LOGISCHE \"0\" ","OFF LOGISCHE \"0\" "]
["M 0.2"]
["M 0.3"]
["M 0.4"]
["M 0.5"]
["M 0.6"]
["M 0.7"]
["M 1.0"]
["M 1.1"]
["M 1.2"]
["M 1.3"]
["M 1.4"]
["M 1.5"]
["M 1.6"]
["M 1.7"]
["M 2.0"]
["M 2.1"]
["M 2.2"]
["M 2.3"]
["M 2.4"]
["M 2.5"]
["M 2.6"]
["M 2.7"]
["M 3.0"]
["M 3.1"]
["M 3.2"]
["M 3.3"]
["M 3.4"]
["M 3.5"]
["M 3.6"]
["M 3.7"]
["M 4.0"]
["M 4.1"]
["M 4.2"]
["M 4.3"]
["M 4.4"]
["M 4.5"]
["M 4.6"]
["M 4.7"]
["M 5.0"]
["M 5.1"]
["M 5.2"]
["M 5.3"]
["M 5.4"]
["M 5.5"]
["M 5.6"]
["M 5.7"]
["M 6.0"]
["M 6.1"]
["M 6.2"]
["M 6.3"]
["M 6.4"]
["M 6.5"]
["M 6.6"]
["M 6.7"]
["M 7.0"]
["M 7.1"]
["M 7.2"]
["M 7.3"]
["M 7.4"]
["M 7.5"]
["M 7.6"]
["M 7.7"]
[]
[null,"PROGRAMMA BOUWSTENEN "]
[]
[";PB10 - PB88 : MOTOREN MET BIJBEHOREND MERKERBYTE (MB10 = MERKERBYTE BIJ PB10)"]
[";PB114 - PB123 : KLEPPEN MET BIJBEHOREND MERKERBYTE "]
[";",";"]
["PB 2","ALARM ACKNOWLEDGE UIT SCADA ","ALARM ACKNOWLEDGE UIT SCADA "]
["PB 4","xxxxxxxxxxxxxxxxx ","xxxxxxxxxxxxxxxxx "]
["PB 5","TEST PROGRAMMA BOUWSTEEN ","TEST PROGRAMMA BOUWSTEEN "]
["PB 9","AUTO START/STOP MOTOREN/KLEPPEN ","AUTO START/STOP MOTOREN/KLEPPEN "]
["PB 10","MM802 - ROERWERK V802 ","MM802 - ROERWERK V802 "]
["PB 11","MM804 - ROERWERK V804 ","MM804 - ROERWERK V804 "]
["PB 12","MP800 - SULFAAT VERLAAD POMP ","MP800 - SULFAAT VERLAAD POMP "]
["PB 16","MP802A - HYDROXIDE DISTRIBUTIE POMP ","MP802A - HYDROXIDE DISTRIBUTIE POMP "]
["PB 17","HC1001 ","HC1001 "]
["PB 18","MK129 - AFZUIG VENTILATOR B129/B130 "," ----SPARE------- "]
["PB 19","MF129 - FILTER BOVEN B129/B130 "," ----SPARE------- "]
["PB 24","MA128 - SLUIS ONDER B128 "," ----SPARE------- "]
["PB 25","MA131 "," ----SPARE------- "]
["PB 26","MK134 - AFZUIG VENTILATOR B134/B135 "," ----SPARE------- "]
["PB 27","MF134 - FILTER BOVEN B134/B135 "," ----SPARE------- "]
["PB 35","MA136 - SLUIS ONDER B136 "," ----SPARE------- "]
["PB 36","MK128 - BLOWER K158 "," ----SPARE------- "]
["PB 37","MK131 - BLOWER K131 "," ----SPARE------- "]
["PB 42 ","MA150 - SCHROEF ONDER B150 ","MA150 - SCHROEF ONDER B150 "]
["PB 43","MA151 - SCHROEF ONDER B151 ","MA151 - SCHROEF ONDER B151 "]
["PB 44","MA161 - SCHROEF ONDER F-150 ","MA161 - SCHROEF ONDER F-150 "]
["PB 45","MA162 - SCHROEF ONDER B162 ","MA162 - SCHROEF ONDER B162 "]
["PB 46","MP804.1 - EIND OXIDATIE FEED POMP ","MP804.1 - EIND OXIDATIE FEED POMP "]
["PB 47","MA182 - SCHROEF ONDER B155 ","MA150.1 - SCHROEF ONDER MA-150"]
["PB 48","MA152 - TRANSPORT SCHROEF ","MA152 - TRANSPORT SCHROEF "]
["PB 49","MA159 - SLUIS ONDER S150 ","MA160.3 - SLUIS ONDER F150 "]
["PB 50","MA160.1 - SLUIS ONDER F150 ","MA160.1 - SLUIS ONDER F150 "]
["PB 52","MA179 - SLUIS ONDER C150 ","MA179 - SLUIS ONDER C150 "]
["PB 53","MA160.2 - SLUIS ONDER F150 ","MA160.2 - SLUIS ONDER F150 "]
["PB 54","MP805 - EVAPORATOR FEED POMP ","MP805 - EVAPORATOR FEED POMP "]
["PB 55","MA153 - SCHREDDER ONDER B153 ","MA153 - SCHREDDER ONDER B153 "]
["PB 56","MK150 - VERBRANDINGSLUCHT VENTILATOR ","MK150 - VERBRANDINGSLUCHT VENTILATOR "]
["PB 57","MK151 - ROOKGAS VENTILATOR ","MK151.1 - ROOKGAS VENTILATOR 1"]
["PB 58","MK152 - LUCHTCOMPRESSOR AANSTEEKBRANDE ","MK152 - LUCHTCOMPRESSOR AANSTEEKBRANDE "]
["PB 59","MA173 - SCHROEF NAAR S159 ","MP804 - POMP NAAR F-840"]
["PB 60","MA152.1 - SCHROEF ONDER MA-152 ","MA152.1 - SCHROEF ONDER MA-152 "]
["PB 61","MA178 - SCHROEF NAAR A173 "," ----SPARE------- "]
["PB 62","MP815 - QUENCH CIRCULATIE POMP ","MP815.1 - QUENCH CIRCULATIE POMP 1"]
["PB 63","MK158 - CONDENSOR VENTILATOR E151\f","MK910 - AANDRIJVING AQUAVANS"]
["PB 64","MP150 - CIRCULATIE POMP ","MK-151.2 - ROOKGASVENTILATOR 2"]
["PB 65","MP151 - CONDENSAAT TRANSPORT POMP ","MP815.2 - QUENCH CIRCULATIE POMP 2"]
["PB 66","MP152 - SUPPLETIE POMP ","MK818.2 - ROOKGAS VENTILATOR 2"]
["PB 68","MA156 - SCHROEF BOVEN BEDVOEDING "]
["PB 69","MP1001 - VASTVERF TOEVOER POMP "," ----SPARE------- "]
["PB 70","MP816A - CIRCULATIE POMP ","MP816A - CIRCULATIE POMP "]
["PB 71","MP816B - CIRCULATIE POMP ","MP816B - CIRCULATIE POMP "]
["PB 72","MK172 - COMPRESSOR K172 ","MK172 - COMPRESSOR K172 "]
["PB 73","MK175 - COMPRESSOR K175 ","MK175 - COMPRESSOR K175 "]
["PB 75","MP950 - SEALWATER POMP ","MP950 - SEALWATER POMP "]
["PB 77","MK820.2 - PRE OXIDATIE BLOWER ","MK820.2 - PRE OXIDATIE BLOWER "]
["PB 78","MP910A - KOELWATER CIRCULATIE POMP ","MP910A - KOELWATER CIRCULATIE POMP "]
["PB 79","MP910S - KOELWATER CIRCULATIE POMP ","MP910S - KOELWATER CIRCULATIE POMP "]
["PB 81","MA157 - BEDVOEDING SLUIS ","XEV157 - SNELSLUITKLEP SLIBS EN SLUDGES "]
["PB 82","MP816C - CIRCULATIE POMP ","MP816C - CIRCULATIE POMP "]
["PB 83","MK818 - ROOKGAS VENTILATOR ","MK818.1 - ROOKGAS VENTILATOR 1"]
["PB 84","MP819 - POST OXIDATIE TANK FEED POMP "," ----SPARE------- "]
["PB 85","MP819.3 - POST OXIDATIE BLOWER "," ----SPARE------- "]
["PB 86","MK820.1 - PRE OXIDATIE BLOWER ","MK820.1 - PRE OXIDATIE BLOWER "]
["PB 87","MB154 - TRILMOTOR BUNKER B154 "," ----SPARE------- "]
["PB 88","MB155 - TRILMOTOR BUNKER B155 "," ----SPARE------- "]
["PB 89","MA168.2 - VOEDINGSSCHROEF NATTE KAT ","MA151.1 SCHROEF ONDER MA151"]
[]
[]
["PB 114","XPV104 - DRIEWEG KLEP NAAR B129/B130 "]
["PB 115","XPV108 - DRIEWEG KLEP NAAR B134/B135 "," ----SPARE------- "]
["PB 116","XEV815 - DEMI-WATER NAAR INLAAT C-815 QU ","XEV815 - DEMI-WATER NAAR INLAAT C-815 QU "]
["PB 117","XPV1008- NATTE KAT TOEVOER KLEP "," ----SPARE------- "]
["PB 118","XEV150 - JALOUZIE KLEP "]
["PB 119","XEV151 - JALOUZIE KLEP "]
["PB 120","PV1008 - VASTVERF TOEVOER KLEP "," ----SPARE------- "]
["PB 121","XPV818 - POT. WATER NAAR S-818/S-822 ","XPV818 - POT. WATER NAAR S-818/S-822 "]
["PB 122","XPV800 - PRODUKT VAN V-800 NAAR TANKAUTO ","XPV800 - PRODUKT VAN V-800 NAAR TANKAUTO "]
["PB 123","XPV182 - BY-PASS CIRCULATIE POMP P150 "]
[";",";",";"]
["PB 150","ANA.IN. EN SCHALEN PW130 - PW254 ","ANA.IN. EN SCHALEN PW130 - PW254"]
["PB 151","ANA.IN. EN SCHALEN QW0 - QW118 ","ANA.IN. EN SCHALEN QW0 - QW118"]
["PB 152","ANA.IN. EN SCHALEN QW128 - QW214","ANA.IN. EN SCHALEN QW128 - QW214"]
["PB 153","ANA.UIT. REGELAARS PW128 - PW200 ","ANA.UIT. REGELAARS PW128 - PW200"]
["PB 155 ","ANA SCALE UI PW 128 - PW200","ANA SCALE UI PW128 - PW200"]
[]
[]
[null,"FUNTIE BOUWSTENEN "," FUNTIE BOUWSTENEN "]
[]
["PB 170","KETEL- EN BRANDERVOORWAARDEN ","KETEL- EN BRANDERVOORWAARDEN "]
["PB 171","REGELAARS NAAR AUTO / SCADA ALARM ACKN. ","REGELAARS NAAR AUTO / SCADA ALARM ACKN. "]
[";;; ",";;; ",";;; "]
["PB 181","SEQ1 - LADEN B129/B130 ","SEQ1 - LADEN B129/B130 "]
["PB 182","SEQ2 - LADEN B134/B135\f","SEQ2 - LADEN B134/B135\f"]
["PB 185","PB 185 PB185 SEQ5 - DOEKENFILTER BESTURING ","PB 185 PB185 SEQ5 - DOEKENFILTER BESTURING "]
[";;; ",";;; ",";;; "]
["FB 4","STATISCHE ","STATISCHE "]
["FB 5","KETELTRIP ","KETELTRIP "]
[";;; ",";;; ",";;; "]
["FB 10","GWS-SEN ","GWS-SEN "]
["FB 11","GWS-SEN ","GWS-SEN "]
["FB 12","GWS-SEN ","GWS-SEN "]
[";;; ",";;; ",";;; "]
["FB 29","BIN-COM ","BIN-COM "]
[";;; ",";;; ",";;; "]
["FB 83","MK 818 STOP ","MK 818 STOP "]
[";;; ",";;; ",";;; "]
["FB 90 ","RESET ","RESET "]
["FB 91","CP143 ","CP143 "]
["FB 92","SET AUTO ","SET AUTO "]
["FB 93","CHK AUTO ","CHK AUTO "]
["FB 94","INT.-ACTUEEL ","INT.-ACTUEEL "]
["FB 99","CYCLIMET ","CYCLIMET "]
[";;; ",";;; ",";;; "]
["FB 101","MOTOR 5 ","MOTOR 5 "]
[";",";",";"]
["FB 111","KLEP 20 ","KLEP 20 "]
["FB 115","NV KLEP 20 ","NV KLEP 20 "]
["FB 119","RESET COMMANDO ","RESET COMMANDO "]
[";",";",";"]
["FB 120","SEND ","SEND "]
["FB 121","RECEIVE ","RECEIVE "]
["FB 122","FETCH ","FETCH "]
["FB 123","CONTROL ","CONTROL "]
["FB 124","RESET ","RESET "]
["FB 125","SYCHRON ","SYCHRON "]
["FB 126","SEND-A ","SEND-A "]
["FB 127","RECEIVE-A ","RECEIVE-A "]
["FB 128","BINAIRE STATISCHE ","BINAIRE STATISCHE "]
["FB 129","RESET BC ","RESET BC "]
[";",";",";"]
["FB 130","ANALOOG IN ","ANALOOG IN "]
["FB 131","P.I.D. IN ","P.I.D. IN "]
["FB 132","P.I.D. OUT","P.I.D. OUT"]
["FB 133","BEREKEN 1 ","BEREKEN 1 "]
["FB 134","BEREKEN 2 ","BEREKEN 2 "]
[";",";",";"]
["FB 140","SEQUENCER 16 ","SEQUENCER 16 "]
["FB 141","SEQUENCER 32 ","SEQUENCER 32 "]
["FB 142","ACT. STOP ","ACT. STOP "]
["FB 143","GENTR ","GENTR "]
["FB 144","KLEPSTAND ","KLEPSTAND "]
[";",";",";"]
["FB 150","ANALOOG INKG ","ANALOOG INKG "]
["FB 151","BEREKEN MEET ","BEREKEN MEET "]
[";",";",";"]
["FB 200","INIT REG ","INIT REG "]
["FB 201","REGELAAR ","REGELAAR "]
["FB 202","SCALE OUT ","SCALE OUT "]
["FB 203","TAKT ","TAKT "]
["FB 204","SPA FB 3","SPA FB 3"]

{"sheet":"Blad2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Blad3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}