{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Subrapport Project"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Subrapport Project","index":0,"n_rows":171,"n_cols":11,"rows_kept":171,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["6","452"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["PLCNaam","Rack","Slot","Opmerking","IOAddress","Aansluitnr","Kanaalnr","Tagnummer_ID","Omschrijving","IOFunctie_ID"]
["6",1,4]
[{"$nulls":4},"100001","1","01","XV-206-01","Ruwwaterafsluiter Filter 6","Dichtmelding"]
[{"$nulls":4},"100002","2","02","XV-206-01","Ruwwaterafsluiter Filter 6","Openmelding"]
[{"$nulls":4},"100003","3","03","XV-206-02","Filtraatafsluiter Filter 6","Dichtmelding"]
[{"$nulls":4},"100004","4","04","XV-206-02","Filtraatafsluiter Filter 6","Openmelding"]
[{"$nulls":4},"100005","5","05","XV-206-03","Inwerkafsluiter Filter 6","Dichtmelding"]
[{"$nulls":4},"100006","6","06","XV-206-03","Inwerkafsluiter Filter 6","Openmelding"]
[{"$nulls":4},"100007","7","07","XV-306-01","Spoelwatertoevoerafsluiter Filter 6","Dichtmelding"]
[{"$nulls":4},"100008","8","08","XV-306-01","Spoelwatertoevoerafsluiter Filter 6","Openmelding"]
[{"$nulls":4},"100009","11","09","XV-306-02","Spoelluchtafsluiter Filter 6","Dichtmelding"]
[{"$nulls":4},"100010","12","10","XV-306-02","Spoelluchtafsluiter Filter 6","Openmelding"]
[{"$nulls":4},"100011","13","11"]
[{"$nulls":4},"100012","14","12"]
[{"$nulls":4},"100013","15","13","QIT-760","Troebelheidsmeting Filter 6","Storing Voeding"]
[{"$nulls":4},"100014","16","14","QIT-760","Troebelheidsmeting Filter 6","Reserve"]
[{"$nulls":4},"100015","17","15","XV-780-02","Filtraatafsluiter Calamiteitenbekken","Dichtmelding"]
[{"$nulls":4},"100016","18","16","XV-780-02","Filtraatafsluiter Calamiteitenbekken","Openmelding"]
[{"$nulls":4},"100017","21","17","LIC-206","Niveau regelaar Filter 6","Storing regelaar"]
[{"$nulls":4},"100018","22","18","P-344","Spoelwaterpomp 1 Filter 6-7","Auto"]
[{"$nulls":4},"100019","23","19"]
[{"$nulls":4},"100020","24","20","P-344","Spoelwaterpomp 1 Filter 6-7","Storing"]
[{"$nulls":4},"100021","25","21","P-344","Spoelwaterpomp 1 Filter 6-7","In bedrijf"]
[{"$nulls":4},"100022","26","22","FITS-780","Debietmeting Filtraat","Storing Voeding"]
[{"$nulls":4},"100023","27","23","FITS-780","Debietmeting Filtraat","Flow puls"]
[{"$nulls":4},"100024","28","24","U-780","UV-unit","In bedrijf"]
[{"$nulls":4},"100025","31","25","U-780","UV-unit","Opwarmingsgereed"]
[{"$nulls":4},"100026","32","26","U-780","UV-unit","Vooralarm"]
[{"$nulls":4},"100027","33","27","U-780","UV-unit","Storing"]
[{"$nulls":4},"100028","34","28","HV 02","Laagspanningsverdeler SPW 2","Hoofdschakelaar In"]
[{"$nulls":4},"100029","35","29"]
[{"$nulls":4},"100030","36","30"]
[null,null,null,"Reserve","100031","37","31","FS-344","Stromingsdetectie Spoelwaterpomp 3","Flowswitch"]
[{"$nulls":4},"100032","38","32","BK 66","Filterkast 6","Afsluiters auto"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["6",1,5]
[{"$nulls":4},"100033","1","01","XV-207-01","Ruwwaterafsluiter Filter 7","Dichtmelding"]
[{"$nulls":4},"100034","2","02","XV-207-01","Ruwwaterafsluiter Filter 7","Openmelding"]
[{"$nulls":4},"100035","3","03","XV-207-02","Filtraatafsluiter Filter 7","Dichtmelding"]
[{"$nulls":4},"100036","4","04","XV-207-02","Filtraatafsluiter Filter 7","Openmelding"]
[{"$nulls":4},"100037","5","05","XV-207-03","Inwerkafsluiter Filter 7","Dichtmelding"]
[{"$nulls":4},"100038","6","06","XV-207-03","Inwerkafsluiter Filter 7","Openmelding"]
[{"$nulls":4},"100039","7","07","XV-307-01","Spoelwatertoevoerafsluiter Filter 7","Dichtmelding"]
[{"$nulls":4},"100040","8","08","XV-307-01","Spoelwatertoevoerafsluiter Filter 7","Openmelding"]
[{"$nulls":4},"100041","11","09","XV-307-02","Spoelluchtafsluiter Filter 7","Dichtmelding"]
[{"$nulls":4},"100042","12","10","XV-307-02","Spoelluchtafsluiter Filter 7","Openmelding"]
[{"$nulls":4},"100043","13","11"]
[{"$nulls":4},"100044","14","12"]
[{"$nulls":4},"100045","15","13","QIT-770","Troebelheidsmeting Filter 7","Storing Voeding"]
[{"$nulls":4},"100046","16","14","QIT-770","Troebelheidsmeting Filter 7","Reserve"]
[{"$nulls":4},"100047","17","15","XV-780-01","Filtraatafsluiter RWK","Dichtmelding"]
[{"$nulls":4},"100048","18","16","XV-780-01","Filtraatafsluiter RWK","Openmelding"]
[{"$nulls":4},"100049","21","17","LIC-207","Niveau regelaar Filter 7","Storing regelaar"]
[{"$nulls":4},"100050","22","18","P-345","Spoelwaterpomp 2 Filter 6-7","Auto"]
[{"$nulls":4},"100051","23","19"]
[{"$nulls":4},"100052","24","20","P-345","Spoelwaterpomp 2 Filter 6-7","Storing"]
[{"$nulls":4},"100053","25","21","P-345","Spoelwaterpomp 2 Filter 6-7","In bedrijf"]
[{"$nulls":4},"100054","26","22","FITS-346","Debietmeting Spoelwater","Storing Voeding"]
[{"$nulls":4},"100055","27","23","FITS-346","Debietmeting Spoelwater","Flow puls"]
[{"$nulls":4},"100056","28","24"]
[{"$nulls":4},"100057","31","25"]
[{"$nulls":4},"100058","32","26"]
[{"$nulls":4},"100059","33","27"]
[null,null,null,"Reserve","100060","34","28","FS-345","Stromingsdetectie Spoelwaterpomp 4","Flowswitch"]
[{"$nulls":4},"100061","35","29"]
[{"$nulls":4},"100062","36","30"]
[{"$nulls":4},"100063","37","31","BK 61","Afsluiters Reinwater","Afsluiters auto"]
[{"$nulls":4},"100064","38","32","BK 67","Filterkast 7","Afsluiters auto"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["6",1,6]
[{"$nulls":4},"100065","1","01"]
[{"$nulls":4},"100066","2","02","V-341","Spoelluchtblower","Auto"]
[{"$nulls":4},"100067","3","03","V-341","Spoelluchtblower","Hand"]
[{"$nulls":4},"100068","4","04","V-341","Spoelluchtblower","Storing"]
[{"$nulls":4},"100069","5","05","V-341","Spoelluchtblower","In bedrijf"]
[{"$nulls":4},"100070","6","06","XV-346","Spoelwaterafsluiter (Vervalllen)","Dichtmelding"]
[{"$nulls":4},"100071","7","07","XV-346","Spoelwaterafsluiter (Vervalllen)","Openmelding"]
[{"$nulls":4},"100072","8","08","BK 06","PLC-paneel Spoelwaterverwerking 2","Spoelprog. actief"]
[{"$nulls":4},"100073","11","09","FIC-346","Debietregelaar Spoelwater","Storing regelaar"]
[{"$nulls":4},"100074","12","10"]
[{"$nulls":4},"100075","13","11"]
[{"$nulls":4},"100076","14","12"]
[{"$nulls":4},"100077","15","13"]
[{"$nulls":4},"100078","16","14"]
[{"$nulls":4},"100079","17","15"]
[{"$nulls":4},"100080","18","16"]
[{"$nulls":4},"100081","21","17"]
[{"$nulls":4},"100082","22","18"]
[{"$nulls":4},"100083","23","19"]
[{"$nulls":4},"100084","24","20"]
[{"$nulls":4},"100085","25","21"]
[{"$nulls":4},"100086","26","22"]
[{"$nulls":4},"100087","27","23",null,null,"Reserve"]
[{"$nulls":4},"100088","28","24",null,null,"Reserve"]
[{"$nulls":4},"100089","31","25",null,null,"Reserve"]
[{"$nulls":4},"100090","32","26",null,null,"Reserve"]
[{"$nulls":4},"100091","33","27",null,null,"Reserve"]
[{"$nulls":4},"100092","34","28",null,null,"Reserve"]
[{"$nulls":4},"100093","35","29",null,null,"Reserve"]
[{"$nulls":4},"100094","36","30",null,null,"Reserve"]
[{"$nulls":4},"100095","37","31",null,null,"Reserve"]
[{"$nulls":4},"100096","38","32",null,null,"Reserve"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["6",1,8]
[{"$nulls":4},"000001","14","01","XV-206-01","Ruwwaterafsluiter Filter 6","Afsluiter openen"]
[{"$nulls":4},"000002","24","02","XV-206-02","Filtraatafsluiter Filter 6","Afsluiter openen"]
[{"$nulls":4},"000003","34","03","XV-206-03","Inwerkafsluiter Filter 6","Afsluiter openen"]
[{"$nulls":4},"000004","44","04","XV-306-01","Spoelwatertoevoerafsluiter Filter 6","Afsluiter openen"]
[{"$nulls":4},"000005","54","05","XV-306-02","Spoelluchtafsluiter Filter 6","Afsluiter openen"]
[{"$nulls":4},"000006","64","06","XV-207-01","Ruwwaterafsluiter Filter 7","Afsluiter openen"]
[{"$nulls":4},"000007","74","07","XV-207-02","Filtraatafsluiter Filter 7","Afsluiter openen"]
[{"$nulls":4},"000008","84","08","XV-207-03","Inwerkafsluiter Filter 7","Afsluiter openen"]
[{"$nulls":4},"000009","94","09","XV-307-01","Spoelwatertoevoerafsluiter Filter 7","Afsluiter openen"]
[{"$nulls":4},"000010","104","10","XV-307-02","Spoelluchtafsluiter Filter 7","Afsluiter openen"]
[{"$nulls":4},"000011","114","11","XV-780-02","Filtraatafsluiter Calamiteitenbekken","Afsluiter openen"]
[{"$nulls":4},"000012","124","12","XV-780-01","Filtraatafsluiter RWK","Afsluiter openen"]
[{"$nulls":4},"000013","134","13"]
[{"$nulls":4},"000014","144","14","V-341","Spoelluchtblower","Commando Auto"]
[{"$nulls":4},"000015","154","15","P-344","Spoelwaterpomp 1 Filter 6-7","Commando Auto"]
[{"$nulls":4},"000016","164","16","P-345","Spoelwaterpomp 2 Filter 6-7","Commando Auto"]
[{"$nulls":4},"000017","174","17","U-780","UV-unit","Commando Auto"]
[{"$nulls":4},"000018","184","18","LCV-206","Regelafsluiter Filter 6","Vast Setpoint"]
[{"$nulls":4},"000019","194","19","LCV-207","Regelafsluiter Filter 7","Vast Setpoint"]
[{"$nulls":4},"000020","204","20"]
[{"$nulls":4},"000021","214","21","BK 06","PLC-paneel Spoelwaterverwerking 2","Blokkeer Filterinst."]
[{"$nulls":4},"000022","224","22","LCV-206","Regelafsluiter Filter 6","Sturing vast"]
[{"$nulls":4},"000023","234","23","LCV-207","Regelafsluiter Filter 7","Sturing vast"]
[{"$nulls":4},"000024","244","24","FCV-346","Regelafsluiter Debiet Spoelwater","Sturing vast"]
[{"$nulls":4},"000025","254","25","FIC-346","Debietregelaar Spoelwater","Regelaar Auto"]
[{"$nulls":4},"000026","264","26"]
[{"$nulls":4},"000027","274","27"]
[{"$nulls":4},"000028","284","28"]
[{"$nulls":4},"000029","294","29"]
[{"$nulls":4},"000030","304","30",null,null,"Reserve"]
[{"$nulls":4},"000031","314","31",null,null,"Reserve"]
[{"$nulls":4},"000032","324","32",null,null,"Reserve"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["6",1,9]
[{"$nulls":4},"300001","1/3","01","LITA-306","Niveaumeting 2 Filter 6","Niveau"]
[{"$nulls":4},"300002","5/7","02","QdPT-306","Weerstandsmeting Filter 6","Verschildruk"]
[{"$nulls":4},"300003","11/13","03","QIT-760","Troebelheidsmeting Filter 6","Troebelheid"]
[null,null,null,"Ook Rec (19)","300004","15/17","04","FITS-780","Debietmeting Filtraat","Debiet"]
[{"$nulls":4},"300005","21/23","05"]
[{"$nulls":4},"300006","25/27","06"]
[{"$nulls":4},"300007","31/33","07"]
[{"$nulls":4},"300008","35/37","08"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["6",1,10]
[{"$nulls":4},"300010","1/3","01","LITA-307","Niveaumeting 2 Filter 7","Niveau"]
[{"$nulls":4},"300011","5/7","02","QdPT-307","Weerstandsmeting Filter 7","Verschildruk"]
[{"$nulls":4},"300012","11/13","03","QIT-770","Troebelheidsmeting Filter 7","Troebelheid"]
[null,null,null,"Ook Rec (18)","300013","15/17","04","FITS-346","Debietmeting Spoelwater","Debiet"]
[{"$nulls":4},"300014","21/23","05","U-780","UV-unit","Temperatuur"]
[{"$nulls":4},"300015","25/27","06","U-780","UV-unit","Lichtintensiteit"]
[{"$nulls":4},"300016","31/33","07"]
[{"$nulls":4},"300017","35/37","08","FIC-346","Debietregelaar Spoelwater","Regelsignaal"]
[{"$nulls":10},"Projectnaam"]
[{"$nulls":10},"108015 - WPB Wouw - Renovatie"]
["6",1,11]
[{"$nulls":4},"400001","9/10","01","FCV-346","Regelafsluiter Debiet Spoelwater","Regelsignaal"]
[{"$nulls":4},"400002","19/20","02"]
[{"$nulls":4},"400003","29/30","03"]
[{"$nulls":4},"400004","39/40","04"]