{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Communicatie PLC02_OPIR"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Communicatie PLC02_OPIR","index":0,"n_rows":65535,"n_cols":6,"rows_kept":65535,"cut":false,"hidden":false,"merged":[[54,1,61,3]],"flags":["formulas_cached_only"]}
[null,"PLC Productie","==>","OPIR","==>","PLC Productie"]
["IP-adres","10.70.1.202",null,"10.70.1.141",null,"10.70.1.202"]
["Register adres",{"$nulls":4},"Register adres"]
[406400,{"$nulls":4},406430]
["Bitpos.  LSB   1",{"$nulls":4},"Bitpos.  LSB    1"]
[2,{"$nulls":4},2]
[3,{"$nulls":4},3]
[4,{"$nulls":4},4]
[5,{"$nulls":4},5]
[6,{"$nulls":4},6]
[7,{"$nulls":4},7]
[8,{"$nulls":4},8]
[9,"Hartslag 1=>0=>1",null,"Hartslag(volgt PLC)",null,9]
[10,"1 : Keuze OPIR",null,null,null,10]
[11,"RWK 5 in",null,null,null,11]
[12,"RWK 6 in",null,null,null,12]
[13,"RWK 7 in",null,null,null,13]
[14,"RWK 8 in",null,null,null,14]
[15,"RWK 11 in",null,null,null,15]
["Bitpos.  MSB   16",{"$nulls":4},"Bitpos.  MSB  16"]
[406401,"Min.aantal filters",null,"Gewenst aantal filters",null,406431]
[406402,"Actueel niveau RWK5  [m3]",null,"Gewenst debiet [m3/h]",null,406432]
[406403,{"$nulls":4},406433]
[406404,"Actueel niveau RWK6  [m3]",null,"Reserve",null,406434]
[406405,null,null,"Reserve",null,406435]
[406406,"Actueel niveau RWK7  [m3]",null,"Reserve",null,406436]
[406407,null,null,"Reserve",null,406437]
[406408,"Actueel niveau RWK8  [m3]",null,"Reserve",null,406438]
[406409,null,null,"Reserve",null,406439]
[406410,"Actueel niveau RWK11  [m3]",null,"Reserve",null,406440]
[406411,null,null,"Reserve",null,406441]
[406412,"Berekend transporttotaal [m3/h]",null,"Reserve",null,406442]
[406413,null,null,"Reserve",null,406443]
[406414,"Productie totaal  [m3/h]",null,"Reserve",null,406444]
[406415,null,null,"Reserve",null,406445]
[406416,"PLC klok : Jaar  (2007)",null,"Reserve",null,406446]
[406417,"PLC klok : Maand ( 1 .. 12)",null,"Reserve",null,406447]
[406418,"PLC klok : Dag  (1..31)",null,"Reserve",null,406448]
[406419,"PLC klok : Uur  (0..23)",null,"Reserve",null,406449]
[406420,"PLC klok : Minuut  (0..59)",null,"Reserve",null,406450]
[406421,"PLC klok : Seconde  (0..59)"]
[406422,"Reserve"]
[406423,"Reserve"]
[406424,"Reserve"]
[406425,"Reserve"]
[406426,"Reserve"]
[406427,"Reserve"]
[406428,"Reserve"]
[406429,"Reserve"]
[]
[null,"Integer"]
[null,"Real : 2 registers"]
[]
[]
[null,"PLC  toggled bit 0 : OPIR leest dit bit uit, voert diverse actie's uit en  kopieert het hartslag bit weer naar de PLC,waarna de PLC dit bit weer toggled.Indien na .. Sec. bit 0 niet wijzigt dan volgt er een communicatie alarm op SCADA.Verder geen actie."]
[]
[]
[]
["Hartslag"]
{"$rows_empty":65475}
[{"$nulls":5},1]