[image: image39.jpg]"

.
TECNOMATIX
NK7.5

Serial Number: 124280F5
Release: 7.5.1 for Microsoft Windows

>  Gopyrn 2004 Tessomatx
"_ Technoiogies Liz. All ighis reserved.

Teonamta s FaciyLnk are

UGS et Tasamars o Tenarats

Teohnoogsa i, Al ot ogos a8

T RM Conpry propany of i respectve ouners.





[image: image1.jpg]A

Tecnomatix




FactoryLink SAPI Protocol Driver
for

FactoryLink 7.x.x

[image: image8.png]



[image: image2.png]


 SAPI_S7
Version 1.0

Printed: Wednesday, December 29, 1999

Table of Contents

51.
Introduction

1.1.
Scope of this document
5
2.
Installation
7
2.1.
Installation of the FactoryLink software
7
2.2.
Installation of the protection
9
2.2.1.
The DeltaLink option file
9
2.2.2.
Demo installation
9
3.
Principle
10
3.1.
The Translator RAPD driver principle
10
3.2.
S7 Communication Principle
11
3.2.1.
Siemens Softnet
11
3.2.2.
Datasets
11
3.2.3.
Virtual connection
12
3.2.4.
Block read and block write
12
3.2.5.
Exception write
13
3.2.6.
Encoded write
13
3.2.7.
Unsolicited receive
13
3.2.8.
Cyclic Read
14
4.
Configuration tables
16
4.1.
Mailbox definition
16
4.2.
Ioxlator definition
17
4.3.
Device definition
18
4.4.
Dataset definition
21
Appendix A. The delta.opt file
24
Appendix B. Command line parameters
26
Appendix C. S7 error codes
27
Appendix D. Messages
31
Appendix E. Configuring Softnet
34
Appendix F. Encoded write lay-out
35
Appendix F. Debug Viewer
38
Introduction
38
DebugView Capture
38
Installation and Use
38
Appendix G. Blackbox crash handler
40
Introduction
40
Usage
40



SAPI Protocol Driver
Provides the following features:

· Supports the S7-300/400 PLC range.

· Runs on Siemens Softnet, which supplies range of different network types and protocols.

· Implements the RAPD driver principle of Usdata, which means that this driver communicates with the IOXlator.

· Full asynchronic communication on Read, Write and Receive.

· Implements the cyclic read functionality for very fast communication.

· Selectable boards. Makes it possible to have more then one board in the same PC, and even switch communication from one board to another.

· Full control over communication.

· Enable tags on all functions per PLC.

· Ease of use. Just specify which areas to Read, Write or Receive.

Third Party Software / Hardware Dependencies:

· Siemens communication board, choice depends on network type: CP1413, CP1416 for Ethernet or TCP/IP, CP5412, CP5611, CP5613 for Profibus.

For TCP/IP you can also use standard ethernetcards supported by the platform.

· Programmable Logic controller of type Siemens S7 300/400 series. PLC’s must be equipped with a communication card, e.g. CP143 (Ethernet).

Supported Protocols:

· Supports the protocols supplied by Siemens Softnet which can be of the following: Profibus, MPI, Industrial Ethernet (TP4 or TCP/IP).


Introduction

Thank you for buying this driver! We hope you will enjoy using this product.


Scope of this document

This manual is written for a technician who is familiar with both the FactoryLink® software and the Siemens S7 or Siemens Programmable Logic Controllers (PLC's). This document can be used both as a training manual as well as a reference manual.

The first section of this manual deals with the installation of Siemens S7 driver. Note that for installation of a complete working system also the Softnet product of Siemens has to be installed. Make sure to install this first according to the documentation of Siemens Softnet.

The second part explains the operation principles of the communication with the Siemens PLC and the translator. Here all terms and definitions are explained to the reader. It ex​plains terms like "Dataset" and "Virtual Connections'. This part should be read by both the PLC programmer and the FactoryLink programmer to make sure that the optimum per​for​man​ce can be achieved.

The third part explains the exact tables associated with this driver. This part is useful only to FactoryLink programmers and can be used as a reference. This part is also an example of how to use this driver with a translator like the ioxlator. It shows the entries made for the pre-configu​red demo, which comes with this package. The demo pro​gram can be used to check if the com​munication is working without making a complete application.

The last part is the appendices, which contain summarised data.

®Copyright1999 by DeltaLink bv, The Netherlands. All rights reserved.

DeltaLink is a registered trademark, The Netherlands.

FactoryLink is a registered trademark of United States Data Corporation, Richardson Texas USA.

DeltaLink bv, Pioenroosstraat 26, 5241AB Rosmalen, The Netherlands, 

tel + 31 73 523 1234

fax +31 73 523 1222

This page is left blank intentionally.


Installation


Installation of the FactoryLink software

To install the FactoryLink task and its related tables please execute the following steps.

Before installing

Before installing the driver on the system, FactoryLink must have been installed error free. It is very important that all the environment settings are set for the FactoryLink system such as the FLINK, FLOPT etc.

First

Copy the files from the "DeltaLink S7 driver" media to the appropriate directories. This will be done automatically by running the install utility placed on the installation media. 

For the Windows platform go to the directory with the install build and execute the following command:

installSYMBOL 195 \f "Wingdings"
Second

After you installed the software you need to activate the tables in the FactoryLink Con​fi​gu​ra​tion Manager (FLCM). The installation utility automatically appends the sapi_s7.ac entry into the {FLINK}/ac/titles file
. The place of this entry is also the place where the option appears in the FLCM Main Menu. Therefore check the validity of the entry and move it to the place where you want to appear it in the Configuration Manager. The entry must match the sapi_s7 entry in the following table

file {FLINK}/ac/titles

...

windhdr.ac

Ioxlator.ac

sapi_s7.ac

spool.ac

...

Third

To make sure all the Configuration Tables (CT's) are generated after a change, the install utility automatically adds the sapi_s7 entry at the end of the {FLINK}/ctgen/ctlist file. The place of this entry is not important. Check if this entry has the same format as in the next table.

file {FLINK}/ctgen/ctlist

...

recipe rcphdr rcpovr

Ioxlator Ioxlatorm Ioxlatorp Ioxlatord Ioxlatort

sapi_s7 sapis7d sapis7p sapis7x sapis7m

iml imltags imltrig

...

Fourth

To enable the help functionality for the Siemens S7 driver tables in the Configuration Manager, the install utility reindexes the ‘help-index’ for the Configuration Manager. If desired reindexing of the ‘help-index’ can be started from the command line prompt.

mkhelpSYMBOL 195 \f "Wingdings"
Fifth
The FactoryLink Configuration Manager uses a map file, {FLINK}/ac/ac2ct.map, to be aware of the different confi​gu​ra​tion tables which can be located behind one entry in the main menu. Upon startup, the Configuration Manager reads the map file instead of all the table configuration files, mainly because reading all these files at once takes too much time. An account manager utility is present to update this conversion file, and can be started from the command line. This utility will also be started automatically from the install utility.

acctmgr  -c -d -t{FLINK}/ac/titlesSYMBOL 195 \f "Wingdings"
Sixth
The protocol driver must, with the FactoryLink Configuration Manager (FLCM),  be entered in the System Configuration table. An entry of an existing task which will not be used at run-time can be overwritten or a new entry can be created with (as a minimum) the following data

Task Name
Description   ....   



Executable File

Sapi_s7
Siemens Sapi S7 Protocol Driver

bin/sapi_s7

The Task Name and name of the executable file are fixed and should not be altered by the user.

This completes the installation of the FactoryLink (software) parts.


Installation of the protection

The S7 driver is protected via the DeltaLink option file. This file contains authorization sequence codes for DeltaLink modules. The protection is linked with the serial number of the FactoryLink package.

AUTONUMLGL
The DeltaLink option file

The installation build of the S7 driver contains an option file, named delta.opt, in the opt direc​to​ry. This file contains the unique autho​ri​za​tion sequence which enables the Sapi S7 driver to run unlimited. The install utility automatically copies the authorization sequence into the {FLOPT}/delta.opt file. It is also possible to enter the authorization sequence manually into the {FLOPT}/delta.opt file. For more information on the delta.opt file refer to Appendix B.

Note that the task will only run on the FactoryLink system with the same serial number. The delta.opt file on the installation diskette contains, for reference, the serial number of FactoryLink.

AUTONUMLGL
Demo installation

It is possible to install the S7 driver without an authorization code. This will be done from a normal installation media. In this case the task will start up but only runs in so called 'demo' mode. This means that the driver runs only for a limited period of time (five hours). After this period has expired the task will shutdown and can not be restarted before the complete FactoryLink system has been restarted. 

After installation of this demo version an authorization code can be ordered and installed which enables the task to run without the time and restart limitation. The authorization code must be entered manually in the {FLOPT}/delta.opt file. For more information on entering the authorization code in the delta.opt file refer to Appendix B. 

The limitations of a demo version of the Siemens Sapi S7 driver are:

- five hours of consecutive run-time

- not restartable (FactoryLink must be restarted)

Note that when authorizing the S7 driver only the authorization code has to be entered, the driver need not to be installed again.


Principle

AUTONUMLGL
The Translator RAPD driver principle

RAPD stands for Rapid Application Protocol Driver. The RAPD principle was adopted so that protocol drivers can be easily and rapidly configured for a FactoryLink application. RAPD is based on the Intertask Mail Exchange Standard or IMX, which defines a way for a protocol driver task to com​mu​ni​ca​te with an I/O translator task (e.g. Ioxlator, high speed logger). The RAPD system consists of a protocol driver which communicates with external devices (RTUs, PLCs, etc.) and a translator which controls data storage (going to and coming from a protocol driver) in the FactoryLink real-time database. All data collected by the protocol driver is referenced as contiguous blocks or ranges within the device. This enables communications between the driver and a device to be very efficient. All data is referenced between the driver and the translator in terms of datasets. Datasets, described in the next section, define memory regions or locations of data within a device.

The protocol driver and the translator communicate with each another via FactoryLink mailbox tags, according to the IMX standard. Every task (translator and protocol drivers) has its own mailbox, so for full communication between a translator and a protocol driver a mailbox database element for every task has to be defined. The IMX standard is especially designed for the following situation. To use one translator and several protocol drivers. For example the translator together with the S7 protocol driver and the Modbus Plus protocol driver. Aside from storage duties, the translator provides data conversions (i.e. analog, IEEE conversions, etc.) for I/O data to/from a protocol driver.


[image: image3.wmf]SAPI S7

protocol

driver

IOXLATOR

Tags

IMX Mailbox


Figure 4.1.1 The RAPD principle.

AUTONUMLGL
S7 Communication Principle

AUTONUMLGL
Siemens Softnet

The DeltaLink S7 driver has been developed on top of Softnet from Siemens, using the SAPI interface. The abreviation SAPI stands for Simple Aplication Programmers Interface and is an generic interface for use with different protocols. This means that the S7 driver is capable of driving different protocols just by installing the correct version of Softnet.

At the moment it is possible to use the S7 driver with industrial ethernet (TP4 or TCP/IP), profibus or MPI. Just by selecting the right communication protocol within Softnet these options become possible. The S7 driver will be configured independently from the type of communication protocol. Only references will be made to addressing information configured in Softnet. This means that the S7 driver is completely unaware of which communication protocol is being used. It is possible to change from one communication stack to another without changing the configuration of the S7 driver. For more information on Softnet refer to the Siemens documentation on this subject.

AUTONUMLGL
Datasets

A dataset is a contiguous area of data in the PLC, which has certain characteristics such as a boundary, start and length. The S7 driver can operate on this dataset by performing IMX commands, which can be reading, writing or unsolicited receiving. The dataset will be uniquely identified by the dataset control tag, which will be defined in the S7 driver. Only one unique dataset control tag per dataset must be defined because it will refer to the data area in the PLC.

Operations on data within a dataset will be done outside the S7 driver by a translator module. This module will extract single elements from the dataset and convert them to the correct type. Datasets of the S7 driver can be of the following type:

	Siemens S7data type
	

	Data type entry
	Description

	DB
	Data Block

	FB
	Flag byte

	IB
	Input byte

	OB
	Output byte

	PB
	Peripheral byte

	CW
	Counter word

	TW
	Timer word

	SW
	System Data word

	DX
	Expanded Data Block

	DE
	Datablock in extended memory

	EB
	Expanded Peripheral byte


Table 3.2.2.1 Dataset types


Virtual connection

The S7 module uses virtual connections to communicate with the PLC. Per PLC one connection has to be established over which all IMX services will execute. The following services are supported:

	Read/Write Service
	Supported

	Block read
	Yes

	Block write
	Yes

	Exception write
	Yes

	Encoded write
	Yes

	Unsolicited Receive
	Yes

	Cyclic Read
	Yes


Table 3.2.3.1 Services supported

Before communication can take place, a connection has to be established with the PLC. To establish this connection addressing information on how to reach the PLC has to be configured. This addressing information will not be configured in the S7 driver but in the Softnet product of Siemens. This addressing information differs according to the protocol stack chosen within Softnet. Within Softnet two utilities must to be used for configuration: Setting the PG/PC Interface and the COML S7 utility. The first utility is to choose the communication stack and card being used, the second to enter addressing information for connections. These connections will be given a logical name. For more information on how to configure Softnet refer to the Siemens documentation on this subject.

In the configuration panels of the S7 driver, connections will be addressed by referring to the logical connection name in Softnet. Each PLC must be related with a unique logical connection name. This name must be entered in the Connection field of the Siemens SAPI device definition. This means that the S7 driver is unaware of which protocol stack is being used. This way it is very easy to exchange protocol stacks.


Block read and block write

The block read and block write commands are performed on a contiguous block of data in the PLC: the dataset. The FactoryLink station initiates both commands. The translator module sends re​quests to the S7 driver for reading or writing an entire dataset. For configu​ring the translator refer to the manual of the translator. The S7 driver will perform the requested command and send a reply of the command back to the translator.


Exception write

An exception write is initiated by the FactoryLink workstation, and writes data to the PLC. Not a complete dataset but one element from the dataset is written to the PLC. The protocol driver will receive a request for an exception write from the translator. The first action the driver will take is to check if the write can be accomplished with one write or must be read first.

If the exception data element size is smaller than the size of the PLC data type element (boundary) the data must be read first, patched with exception data and written back. If this is not done, data will be unintentionally overwritten in the PLC. Whether this is the case depends on the data type of the dataset.

For example a S7 plc with a bit in a Data Block (DB) has to be set then the specific data byte has to be read first because the smallest element in a Data Block is a byte. The bit has to be patched into the byte and written back.

In the example mentioned above it is possible, that the device changes the contents of the byte after the driver has read the byte but before the new value is written. This means that after the write of the protocol driver the content change of the PLC is lost. For applications which require that single elements can be accessed both by the PLC and the S7 driver, an encoded write can be used. The encoded write will be discussed in the next section.


Encoded write

The encoded write function is almost similar to the exception write in the fact that both functions write single data elements on exception. The difference is that the exception write accesses directly the destination address in the PLC whereas the encoded write composes an encoded write command and writes this command to a location in a certain data block. The PLC program reads and decodes this encoded write command and accesses the actual destination location.

The advantage of this method is that for every element to write only one write command is needed because the PLC program does the actual operation on the data element (no reading before writing). Another advantage is that the PLC program can control all encoded writes because they all are written to one location in the PLC. 

The location where the encoded write command will be placed is part of the definition of a logical device; a detailed description is in the next chapter.


Unsolicited receive

In case of an unsolicited receive the PLC sends a dataset to the FactoryLink workstation, without a specific request from that workstation. This means that the action is initiated by the PLC. The protocol driver will check if the received data is configured in one of the datasets. If this is the case then the data will be sent with the dataset information to the translator which con​verts and updates the data. If no dataset is specified regarding to the received data, the data will be discarded.

The unsolicited receive function is a very powerful functionality for fast communication be​cau​se no request has to be placed by the protocol driver. This way less overhead is invol​ved in communication. Data which alters unpredictably such as alarms are very suitable for the unsolicited receive function. Some extra programming effort has to be done in the PLC becau​se the PLC is in charge of sending the data.


Cyclic Read

The cyclic read functionality is a very powerful type of communication implemented by the S7 protocol. The principle of this communication method is as follows: With cyclic read the CP in the PLC is instructed to send data with a fixed interval to the FactoryLink station. This sending must be started and will continue indefinite until a command to stop will be send. This service maps to the IMX unsolicited receive functionality. This means that data received from the cyclic read functionailty will be treated as if it were unsolicited data and forwarded to the translator.

This type of communication has some very big advantages. First of all the CPU load on both the FatoryLink system as the PLC will be reduced. Because the FactoryLink system doesn’t have to initiate IMX requests but only receive unsolicited data, the CPU load will be drastically reduced. The CP on the PLC side will handle complete communication, no additional programming has to be done which also reduces CPU load on the PLC drastically.

Another advantage is that the performance of communication is very high because the unsolicited receive functionality is being used which means that no triggering has to be done on both sides. Together with the ease of configuration, the cyclic read is a very suitable type of communication.

The starting and stopping together with the update interval has to be configured in the S7 driver. This has to be done in the panel Siemens S7 Dataset Definition at the Cyclic Read field. In case the change flag of the tag is set the the S7 driver will read the value of the tag and start the cyclic read with the specified update rate. An update rate of zero means in this case to stop the cyclic read of the dataset.

AUTONUMLGL
FactoryLink domain selection

The standard domain for the S7 driver is the SHARED domain. The protocol driver communicates with a dedicated piece of hardware, therefore only one task should be able to access the hardware. If only one program accesses the hardware, the task should be located in the shared domain and therefore started by the shared runtime-manager.

Important The protocol driver and the translator must be in the same domain ( either SHARED or USER ).


[image: image4.wmf]Protocol

driver

Ioxlator

RTDB

SHARED

Graph

RTDB

USER


Figure 3.3 Standard domain selection.


Configuration tables

In the Configuration Manager Main Menu, select Siemens SAPI S7 Protocol Driver. Four tables appear, with the titles of all panels visible for direct access. To access a specific panel position the cursor on a visible area and press the left mouse-button, or use the Next/Prev but​tons .

Note: For general information about entering data in FactoryLink configuration tables, refer to the FactoryLink Fundamentals Manual.

AUTONUMLGL
Mailbox definition

From the display of all the panels, select the Siemens SAPI Mailbox Definition panel.

The Siemens SAPI mailbox definition panel allows the user to configure one mailbox tag for the SAPI S7 pro​to​col driver. This mailbox will be used by the driver to receive IMX requests from other modules within FactoryLink. Specify the following information.

[image: image9.png]



Figure 4.1.1 DeltaLink SAPI Mailbox Definition.



Protocol Driver Mailbox Tag

Tag name of the SAPI S7 protocol driver mailbox element to be refe​ren​ced by a translator task i.e. the ioxlator module. The ioxlator module uses this mailbox to send requests to the SAPI S7 protocol driver.

entry 

Required.

entry type 
Standard FactoryLink tag name.

valid entry 
MAILBOX.



Description

Description of the SAPI S7 protocol driver mailbox element defined at creation of this tag.

valid entry 
Output only.


Ioxlator definition

From the display of all the panels, select the Siemens SAPI Translator definition panel.

The SAPI S7 Translator Definition panel allows the user to specify one or more translators i.e. the ioxlator. This mailbox will be used by the driver to reply the IMX request to the right translator which will then decode the IMX mailbox message. The panel shows an example of a configuration.

[image: image10.png]BASIMATIC NET  COML S7 -TCPIP.TXT A

File Help
Nods name Network 0
[evi_ton ] [tcene =]
57 connection list Edit 57 connection selected on left

P Hame: PLCT
VFD Name [vFD1

Bemote Addr:  [194.229.87.30

Local TSAP: (hexadecimal)
Remote TSAP: (hexadecimal)

Delete Insert Replace | Cangel





Figure 4.2.1 Siemens SAPI Translator Definition.


Translator Mailbox Tag

Tag name of a translator mailbox tag, i.e. the ioxlator module, to be refe​ren​ced by the S7 module. The S7 module will write IMX responses, which are meant for a specific translator into this mailbox. The translator module uses this mailbox to receive data from the S7 driver and decode this data.

entry 

Required.

entry type 
Standard FactoryLink tag name.

valid entry 
MAILBOX.



Max MSG

The maximum number of messages defines a limit of the number of IMX responses that the translator mailbox can contain. This value has been implemented as a security option to prevent the translator mailbox from filling up. This can happen for some reason in case the translator can not handle all IMX responses fast enough. The number of IMX responses should be monitored at run-time and should be normally zero with occasionally peaks. This value can be tuned depending on these peaks.

entry 

Required / Default 100.

entry type 
Decimal number.

valid entry 
Positive integer 1 .. 9999.



Description

Description of the translator mailbox element defined at tag creation.

valid entry 
Output only.


Device definition

From the display of all the panels, select the Siemens SAPI S7 Device Definition panel.

The Siemens SAPI S7 Device definition panel must be used to specify logical devices to communicate with. The logical device will be related to the Softnet product from Siemens through the Board and Connection field. Within Softnet the actual addressing must be configured according to the type of communication protocol selected, for example profibus or industrial Ethernet.

[image: image11.png]Edt View Uilties Est Help

(O]

Translator Max MSG E
Mailbox Tag
0xLATORMBX 5 ININTT] TOXLATOR Mailbox "

Cancel | | Enter

Next





Figure 4.3.1 DeltaLink SAPI_S7 Device Definition.


Device Name

Logical name to define a communication device. This name will only be used internally in the S7 module and will also appear as the link in the next panel DeltaLink S7 Dataset Definition
entry 

Required.

entry type 
Alphanumeric string.

valid type 
String of up to 16 characters.


*Board

Logical name to select the communication board for use. This logical name must relate to a definition of a board in the Siemens Softnet configuration. This configuration must be done in the utility Setting the PG/PC Interface at the Access Point of Application selection. On how to configure a specific type of communication within the Softnet product of Siemens refer to the documentation of Softnet. This field can be configured either a constant or as a tag. In case a tag has been configured then it is possible to change the communication board at run-time.

entry 

Required.

entry type 
Alphanumeric string or tag name

valid type 
String of up to 16 characters.


Connection

The connection field refers to a connection definition within Softnet. This referral determines to which PLC will be connected and thus communicated with. The entry of this field is a logical name, which must be defined in Softnet. The connection must have been defined in Softnet using the COML S7 utility (SIMATIC NET Configuration Management Local for COML S7). With this utility a connection can be defined or every type of communication. On how to define these connections refer to the documentation of the COML S7 product.

entry 

Required.

entry type 
ASCII string.

valid entry 
String of up to 16 characters.


Comm Type

The S7 module supports two types of communication: CP or CPU. The major difference between the two types is that CP communication handles all the request in the CP module of the PLC i.e. CP434 and the CPU type handles all request in the CPU module of the PLC. Recommended is to use the CP type because almost no configuration in the PLC has to be done and the performance at run-time is higher because there is almost no load on the CPU. In combination with the cyclic read functionality this will give the best performance and CPU load results (on both sides, PLC and PC). The only reason to use the CPU type is because it can handle larger blocks of data.

entry 

Required.

entry type 
Selection key field.

valid entry 
CP or CPU.



Encode DB

This field defines a datablock in the PLC where the encoded write commands will be written to. The encode FB in the PLC will check this datablock for incoming requests and perform the actual writing.

entry 

Optional.

entry type 
Decimal number.

valid entry 
Positive integer 1..255.

[image: image12.png](O]
Edt Vew Uies Ext Heb
Translator Data Set Type | DB | Stat | Length E
Mailbox Tag
DS0 DB 50 0 10
IOXLATORMBX_S | DS1 DB 50 5 1
I0XLATORMBX S | DS2 DB 50 10 14
I0XLATORMBX S | DS3 DB 50 10 14
I0XLATORMBX S | DS4 DB 50 10 14
I0XLATORMBX S | DS5 DB 11 0 12
IOXLATORMBX S | DS6 DB 50 30 36 )
I0XLATORMBX S | DS7 0B 50 30 36
P —
Cancel | | Enter || B | Next Prev.





Figure 4.3.2 DeltaLink SAPI S7 Device Definition.


Status

The S7 driver uses this tag to update the status of the connection with the PLC. A value of zero indicates no error, any other values represents an error. 

entry 

Optional.

entry type 
Standard FactoryLink tag name.

valid entry 
ANALOG.



Cyclic Count

The cyclic count element holds the value of the total number of cyclic count currently active. With this value it can be checked if all values are executing or not.

entry 

Optional.

entry type 
Standard FactoryLink tag name.

valid entry 
ANALOG.



Read disable

Real-time digital database element used to enable/disable read commands for this lo​gi​cal device. Read commands are enabled if there is no tag defined, or the sta​tus of the digital tag is OFF. Read commands are disabled if a tag is defined and the status of the tag is ON.

entry 

Optional.

entry type 
Standard FactoryLink tag name.

valid entry 
DIGITAL.



Write disable

Real-time digital database element used to enable/disable write commands for the lo​gi​cal device. Write commands are enabled if there is no tag defined, or the sta​tus of the digital tag is OFF. Write commands are disabled if a tag is defined and the status of the tag is ON.

entry 

Optional.

entry type 
Standard FactoryLink tag name.

valid entry 
DIGITAL.



Receive disable

Real-time digital database element used to enable/disable receive commands for the lo​gi​cal device. Receive commands are enabled if there is no tag defined, or the sta​tus of the digital tag is OFF. Receive commands are disabled if a tag is defined and the status of the tag is ON.

entry 

Optional.

entry type 
Standard FactoryLink tag name.

valid entry 
DIGITAL.


Dataset definition

From the display of all the panels, select the Siemens SAPI Dataset definition panel. This panel allows the user to specify datasets for a particular lo​​gi​cal device. Different logical device names are selected in the panel Siemens SAPI Device Definition. The name of the logical device is displayed in the field Device Name, at the bottom of the table. 

[image: image13.png]EthemelMAC}Address  Mode | 57-Protocol |

P

Reset
Restat

Test

[OK. Fiestat CF was completed successiul:

Reset CP

Rleset and restat CP.

Functonal test

o'

I]

oK

Cancel Standad_|

Help





Figure 4.4.1 Siemens SAPI Dataset definition.


Translator Mailbox Tag

Translator reply mailbox, the S7 driver will reply IMX responses from this dataset into this mailbox ( N.B. IMX must be supported by the translator task). The translator task will read this mailbox in order to receive IMX responses.

entry 

Required.

entry type 
Standard FactoryLink tag name.

valid entry 
MAILBOX.



Data Set

Specify the dataset control tag in this field. This tag will be used by IMX to uniquely identify this dataset. This tag name will also be referenced in the translator task. This tag must be unique and only be used to identify this dataset throughout the whole application.

entry 

Required.

entry type 
Standard FactoryLink tag name.

valid entry 
DIGITAL.



Type

Data type definition of the data area in the PLC. Note that exception write behaviour depends on the type of data area. To know how an exception write is executed, one should regard the boundary of the data area and the element size involved with the exception write.

entry 

Required.

entry type 
Alphanumeric string.

valid entries 
DB, FB, IB, OB, PB, CW, TW, SW, DX, DE, EB.

	Siemens S7data type
	

	Data type entry
	Description

	DB
	Data Block

	FB
	Flag byte

	IB
	Input byte

	OB
	Output byte

	PB
	Peripheral byte

	CW
	Counter word

	TW
	Timer word

	SW
	System Data word

	DX
	Expanded Data Block

	DE
	Datablock in extended memory

	EB
	Expanded Peripheral byte




DB

Data block number for the datatypes: DB, DE or DX.

entry 

Optional.

entry type 
Decimal number.

valid entry 
Positive integer 1 ..255.



Start

The starting address of the dataset.

entry 

Required / Default 0.

entry type 
Decimal number.

valid entry 
Positive integer 0 ..2048.



Length

The total length of the dataset. This length can be in bytes or in words depending on the data type. For example the length of a dataset will be in words and the length of flag bytes will be in bytes. The reason for this is because a datablock has a word boundary and flag bytes a byte boundary.

entry 

Required / Default 1.

entry type 
Decimal number.

valid entry 
Positive integer 1 ..2048.




Cyclic Read

The cyclic read functionality can be started and stopped via the Cyclic Read tag. In case of starting this tag must hold the interval value with which the CP in the PLC will update the data. The update rate will be set if the change flag of this tag changes. To stop the cyclic read a value of zero must be written into this tag. The update rate is in tenths of seconds for example a value of 10 means 1-second update rate.

entry 

Required / Default 1.

entry type 
Decimal number.

valid entry 
Positive integer 1 ..2048.


Appendix A. The delta.opt file

In order to run the task permanently with full functionality an authorisation sequen​ce for the task option is needed. This appendix describes the authorisation sequence together with the option file.

The authorisation sequence of every independent DeltaLink module must reside in the {FLOPT}/delta.opt file in order to take effect. If  the task has been ordered with an authorisation sequence then this sequence resides on the install diskette (in the /opt/delta.opt file) and will be automatically added to the {FLOPT}/delta.opt file with the installation. If  the task has been previously installed from a demo diskette and the authorisation sequence has been purchased later then the sequence must be added manually to the {FLOPT}/delta.opt file.

The format of the delta.opt file consists of two parts. The first part is the comment header. This part remains always at the beginning of the file. Every line of the comment part starts with an '*' character. The second part contains the authorisation sequences of every indepen​dent DeltaLink module. Every line must hold one sequence code and must apply to a strict format.

An example of the option file looks like this

Protection file delta.opt

*

* Copyright 1998 DeltaLink bv. All Rights Reserved 

*

* DeltaLink bv

* Pioenroosstraat 26 

* NL-5241 AB Rosmalen

* The Netherlands

* Tel (int) 31 73 5231234

* Fax (int) 31 73 5231222

*

*

* FactoryLink Serial Number 12345NTI

*

* DeltaLink module option

*

* MODULE = taskname of always 8 characters with trailing spaces

* .      = <space>

* X      = authorisation code supplied by DeltaLink

*

* MODULE..XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX.XXXX

SAPI__S7 2D6F E047 2534 036E 1215 EC80 92F8 1EFC C4C0

If  a full installation diskette with authorisation has been ordered then the header in the option file on the diskette contains the serial number of FactoryLink. The task will run only on the FactoryLink package with this serial number. If the serial number is not listed in the {FLOPT}/delta.opt file due to a previous demo installation then this number can be added in the header of this file.

The authorisation code must exactly match the format as listed in the header. If this is not the case the module will not recognise the authorisation sequence and start up in demo mode.

The format of an authorisation sequence line is as follows

MODULE<s><s>XXXX<s>XXXX<s>XXXX<s>XXXX<s>XXXX<s>XXXX<s>XXXX<s>XXXX<s>XXXX<CR><LF>

The MODULE field contains the DeltaLink module name in this case SAPI__S7. This field must always be 8 characters long. If the module name is shorter then 8 characters then the name must be filled out with spaces to 8 characters.

After the MODULE field one space must be entered.

After the space field 9 records must be specified with the authorisation code. One record is build up of one leading space (ASCII 0x20) and four sequence codes. The sequence codes must be entered exactly as specified by DeltaLink.

After the authorisation code records a carriage return (ASCII 0x13) and linefeed (ASCII 0x10) must fol​low.

There may be no empty lines between the specification of more than one module. To add an authorisa​tion sequence a normal editor can be used. If all modules with the right authorisation codes are speci​fied according to the format described above then the modules will start with full functionality.

Appendix B. Command line parameters

The protocol driver accepts several command line parameters, these can be configured with the configuration manager in the ‘System Configuration’ table, column ‘Program Arguments’. An argument consists out of first a minus sign (‘-‘), followed by the a letter specifying the option. After the letter an optional number can be present, if this is supported by the option.

	Option
	Description

	
	

	-dn
	Debug option, the level of debug information is set with the number n. The range of this number is from 1 until 9. If no number is specified the default level will be 1. The debug output will be visible in the ‘window’ of the protocol driver, or that of the run time manager.

	
	

	-ln
	Same as the previous option, difference is the output device. For this option an ASCII log file is generated, being the file {FLAPP}/{FLNAME}/{FLDOMAIN}/log/sinec_h1.log

	
	

	-vn
	Debug option, the level of debug information is set with the number n. The range of this number is from 1 until 9. If no number is specified the default level will be 1. The dubug information is sent to the standard debug output of the Microsoft operating system Microsoft supports debugging of applications with a ‘DebugViewer’, an application that is capable of showing, filtering and saving debug information. In your shipment is included a debug viewer application.

	
	

	-LSn
	Local Station id with number n, needed if the Ioxlator and protocol driver reside on different nodes (or FactoryLink workstations). This must be an unique number for the network.

	
	

	-b
	The option – installs a crash handler for the protocol driver. The crash handler will pop up in case of a rash, and will give several options to handle the information collected prior to the crash.


Appendix C. S7 error codes

These error codes will be generated by Softnet and will be returned to the S7 driver which will in turn display them. For more detailed information about these error codes turn to the Softnet documentation.

	Error #
	general errors

	0
	No error

	1
	Unknown error

	2
	Wrong CP description

	3
	No resources available

	7
	Invalid parameter

	8
	Too long data

	9
	Too many DLL users

	10
	Wrong indication confirmation

	11
	Service not supported

	20
	Invalid configuration reference

	23
	Connection name not found

	25
	no connection database file

	30
	invalid order id

	31
	order id already used

	40
	invalid remote order id

	41
	remote order id already used

	42
	no remote order id

	50
	object undefined

	51
	object attributes inconsistent

	53
	object access denied

	80
	invalid data size

	81
	receive buffer is full

	82
	invalid data range or type

	83
	invalid segment

	90
	controller or CMI or FW problems

	100
	error mini DB type

	101
	error mini DB value

	112
	service VFD already used

	113
	service connection already used

	120
	connection arboreta

	121
	invalid connection state

	122
	maximum number of requests reached

	123
	error connection confirmation

	130
	invalid cyclic read state

	140
	error installing

	141
	internal error

	142
	no sinec service

	143
	no license installed

	150
	error symbolic address

	151
	symbolic address inconsistent

	160
	error remote brecv

	161
	error remote bsend

	162
	remote bsend cancelled

	163
	remote database too small

	170
	error no rcv block


The following errors are reported by the S7 driver.

	Error #
	H1 data package errors

	201
	Unidentified data received.

	202
	Encode value not supported.

	203
	Unknown encode type.

	204
	The size of the H1 packet was too small

	205
	Error in received H1 protocol header


	Error #
	H1 data package errors

	300
	No error.

	301
	Incorrect Q/Z type at handling block.

	302
	Area not present in AG.

	303
	Area in AG too small.

	304
	AKD Error in the AG.

	305
	Error with condition code word.

	306
	No valid ORG format.

	307
	No free data buffer.

	308
	No free transport links.

	309
	Remote error with Read/Write.

	310
	Data Link error.

	311
	Handshake error.

	312
	Initiation error.

	313
	Abort after reset.

	314
	Job with bootstrap function.

	315
	Job not present.

	316
	Area in AG too small.


	Error #
	FactoryLink errors

	401
	Internal error

	402
	Out of memory

	403
	Operating system error

	404
	Initialization not successful

	405
	Initialization not successful

	406
	Incorrect function

	407
	Incorrect argument

	408
	Incorrect data

	409
	Bad tag

	410
	Null pointer assignment

	411
	Change flag not set

	412
	Procedure table full

	413
	Bad procedure name

	414
	Bad user name

	415
	Bad option

	416
	Incorrect checksum

	417
	No options

	418
	No key

	419
	Bad key

	420
	No port available

	421
	Port busy

	422
	FL already active

	423
	No lock

	424
	Lock failed

	425
	Lock expired

	426
	Wait failed

	427
	Termination flag set

	428
	Q-size to big

	429
	Q-size changed

	430
	No tag list

	431
	Tag list changed

	432
	Wake up failed

	433
	No signals

	434
	Signaled

	435
	Not a mailbox

	436
	No messages

	437
	Access denied

	438
	Attribute failure

	439
	Invalid attribute

	440
	Attribute not defined

	441
	Application exists

	442
	RTDB does not exist

	443
	No task bit

	444
	Not a lite task


	Error #
	IMX errors

	450
	Bad message type

	451
	Message with dataset control tag not found in queue

	452
	No messages available to query

	453
	Bad receive mailbox tag

	454
	Bad mailbox send tag

	455
	Bad dataset control tag

	456
	Message cannot be adjusted

	457
	Operation to big for variable

	458
	Unknown boundary

	459
	Function not supported

	460
	No message for this index present

	461
	The remote dataset Is not defined on this system

	462
	The received dataset was not registered

	463
	The message is not queued

	464
	Message is rejected due error in the remote IMX

	465
	Illegal method of addressing bits on bit boundary

	466
	Element cannot be written

	467
	Invalid buffer specified

	468
	Block write function impossible

	469
	Maximum number of messages in MBX reached

	470
	No memory left

	471
	Error registering standard dataset

	472
	Error writing message in pipe

	473
	Not supported IMX message

	474
	Error creating pipe

	475
	Error starting threat

	476
	Error server connecting to pipe

	477
	Error child connecting to pipe

	478
	Error reading the pipe

	479
	Error number of bytes read from pipe

	480
	Error writing into the pipe

	481
	Error number of bytes written into the pipe

	482
	Error reading dataset from the mailbox

	483
	No communication buffers assigned

	484
	Error decrementing semaphore

	485
	Error writing to pipe, no space left

	486
	Error querying no. of messages for Ioxlator

	487
	Max. No. of messages in Ioxlator MBX reached


	Error #
	S7 driver errors

	850
	read functionality has been disabled 

	851
	write functionality has been disabled

	852
	unsolicited receive has been disabled

	853
	invalid addressing method on bit boundary

	854
	exception write not possible to destination

	855
	S7 driver has shutdown

	856
	an unknown error occured in the comm layer 

	857
	no data received 

	859
	encoded write is not possible

	861
	no connection established

	862
	communication board not defined in Softnet

	863
	connection not defined in Softnet

	864
	invalid cyclic read interval

	865
	error starting the cyclic read cycle

	866
	error stopping the cyclic read cycle

	867
	maximum of cyclic reads reached

	870
	wrong response received with request

	871
	request timed out 


Appendix D. Messages

If an error condition occurs in the protocol driver task during run-time mode, a message to that effect will appear on the runtime manager graphics screen to the right of "SAPI_S7". The error messages that may be displayed are as follows

Running in DEMO mode

The task did not find the DeltaLink authorization code at start up. This is a non fatal error, however the task continues running in DEMO mode. The DEMO mode has a limitation timed for 5 hours. After shutdown the task can not be restarted without stopping the complete FactoryLink application.
Demo shutdown, licensed to run 5 hours

The task did not find the DeltaLink authorization code, when starting up and continued running in DEMO mode. The DEMO has a limitation timed for 5 hours. After shutdown the task can not be restarted without stopping the complete FactoryLink application.

Demo restart prohibited, restart FactoryLink

The task did not find the DeltaLink protection code, when starting up. The option file could not be present or damaged. This is a non fatal error, however the task continues running in DEMO mode. The DEMO has a limitation timed for 5 hours. After shutdown the task can not be restarted without stopping the complete FactoryLink application.
Out of RAM

There is not enough RAM memory to load the complete configuration and/or task. This is a fatal error.

Error (%d) reading RTDB element

An error occurred reading a tag value. The error number is displayed.

Error (%d) forcing RTDB element

An error occurred forcing a tag value. The error number is displayed.

Error (%d) writing RTDB element

An error occurred writing a tag value. The error number is displayed.

Error (%d) retrieving event

An error occurred while waiting for an event to happen. The error number is displayed.

Can't open CT file

The task was unable to open the configuration table file, generally because it does not exist. This is a fatal error. Check the $FLINK/ctgen/ctlist file fo the sapi_s7 entry or try to generate the file with the ctgen utility

No triggers defined

The task was able to open the configuration table file, but contained not enough information to continue running. This is a fatal error.

Error reading CT index

An error occurred reading the index of the CT file. The sapi_s7 ct file is probably corrupted, try to generate new one with the ctgen utility. This is a fatal error.

Error reading CT header

An error occurred reading the header of a table in the CT file. The sapi_s7 ct file is probably corrupted, try to generate new one with the ctgen utility. This is a fatal error.

Error reading CT record

An error occurred reading a record of a table in the CT file. The sapi_s7 ct file is probably corrupted, try to generate new one with the ctgen utility. This is a fatal error.

Initialization critical parameters failed

Use of critical sections will not be possible, but is still required for full functionality of the pro​to​col driver. Try stopping the complete appliaction and start up again. This is a fatal error.

Event not registered to FL kernel

Tag event is not registered to the FactoryLink kernel. This is a fatal error.

No Ioxlators defined

There are no Ioxlators (or mailbox) defined. Ckeck the configuartion panels of the S7 driver. This is a fatal error.

No datasets defined

No dataset is defined, the protocol driver has nothing to do. Therefore this considered to be a fatal error.

Unknown Ioxlator table %s record %d type %d

The protocol driver configuration table file contains an unknown Ioxlator mailbox tag, for the specified table, record number and type of dataset. This is a fatal error.

IMX Bad Mailbox TAG table %s record %d type %d

IMX error, internal error of the protocol driver task. Specified are table number, record number and type number.

IMX dataset not unique %s

IMX error, dataset control tag is not unique, the name of the dataset control tag is specified. This is a fatal error, a dataset control tag can only be used once, to define a dataset!

IMX (%d) Initialization failed

IMX initialization failed, the error number is reported. This is a fatal error.

IMX (%d) dataset registration failed %s

Registration of the reported dataset failed, the cause can be determined by the error number. This is a fatal error.

IMX semaphore creation failed

Creation of semaphores, needed for IMX failed. This is a fatal error.

IMX failed to start thread

The protocol driver could not start a thread. This is a fatal error.

IMX maximum msg for Ioxlator %d reached

The reported Ioxlator failed to process the queued messages, the configured maximum length of the queue is reached. The protocol driver stops queuing until the number de​creases.

IMX (%d) send error to mailbox %s

The protocol driver could not queue a message for the reported Ioxlator due to an error, the corresponding error number is reported.

IMX (%d) reply to mailbox %s

The protocol driver could not queue a message for the reported Ioxlator due to an error, the corresponding error number is reported.

Com building device failed

Communication error building of a communication device failed. This is a fatal error.

Com unknown DataSet of type %d

Unknown dataset type specified, the type invalid type id is reported. This is a fatal error.
Com init comm. layer %d

An error occurred during initialising the communication layer Specified is the error num​ber.

Com (%d) connecting ‘%s’ %s

An error occurred during connecting to a device. Specified are the device name, func​tio​nality and the error number.

Com (%d) listenening %s %s

An error occurred during listening. Specified is the error number.

Com (%d) accepting connection %s

An error occurred during accepting a connection to a device. Specified are the device name and the error number.

Com (%d) disconnecting ‘%s’ %d

An error occurred during disconnecting from a device. Specified are the device name, functionality and the error number.

Com (%d) read %s

An error occurred during reading from a device. Specified are the device name and the error number.

Com (%d) reading for exception %s

An error occurred during reading from a device for an exception write. Specified are the device name and the error number.

Com (%d) encode write %s

An error occurred during writing for an encoded write to a device. Specified are the device name and the error number.

Com (%d) write %s

An error occurred during writing to a device. Specified are the device name and the error number.

Com (%d) receive %s

An error occurred during receiving from a device. Specified are the device name and the error number.

Com (%d) reject connection %s, %s

An incoming connection request is rejected. Specified is the error number.

Appendix E. Configuring Softnet

The S7 driver uses Softnet as the protocol stack for communication with the PLC’s. In order to use Softnet with the S7 driver it has to be configured. First step in configuring softnet is to point out which adapter and protocol to use. This must be done via the Setting the PG/PC Interface utility of Softnet.

[image: image14.png](O]

Edt View Uilties Est Help

Device Name. *Board Read Connection Write Connection Receive Connection Encode DB

[TET | cP_H1_: READ WRITE RECEIVE 1

Cancel | | Enter | Next Prev





Figure E.1 Setting the PG/PC Interface utility

The install button allows you to choose a communication adapter and protocol first. When the install button is pressed then the window as shown in figure E.2 will pop up. Add here the board and protocol that you will be using. Then close the window again.

In the main window choose now the right protocol adapter combination in the Module Parameter Set Used list box and press the Properties button. The back window of figure E.1 will pop up. At the S7- Protocol tab check Activate S7. At the SAPI-S7 Database entry a configuration database which is generated with the COML S7 must be specified. At this moment this database doesn’t exist because we didn’t configure it yet. The future database location and name can be configured here or it can be configured later.

The value listed at Access Point of Application is very important because it has to be referenced in the S7 driver configuration. This value must be specified in the panel Siemens SAPI Device Definition at the Board field ( see section 4.3).

[image: image15.png]8 Siemens API Device def
Edt View Uilties Est Help

(O]

Receive Connection Encode DB Status. Read Disable Disable Rev Disable
RECEVE 1 ]
Cancel Enter Exit Next Prev.





Figure E.2 Installing adapter and protocol

Addressing information per PLC has to be configured after setting the PG/PC interface. This must be done with COML S7 utility from Softnet. Per plc on logical connection must be configured as shown in figure E.3.

At the section Node name the name of the connection database must be specified. This must be the same name as the SAPI S7 database in figure E.1. At Network type the same type of protocol must be specified as in figure E.2. Next step is to configure one logical connection for each PLC on the network. This must be done on the right side of the window. The value at the name section is very important because it has to be referenced in the S7 driver. This value must be specified in the panel Siemens SAPI Device Definition at the Connection field ( see section 4.3) and is the relation of the addressing information of the PLC.

[image: image16.png]



Figure E.3 COML S7 utility

Appendix F. Encoded write lay-out

The S7 driver is capable to perform an encoded write. An encoded write causes the protocol driver to place coded information in a data block in the PLC instead of di​rect​ly updating or changing a variable. 

The information, placed in the PLC by an encoded write, should be decoded by a PLC-pro​gram in order to update/change the correct variable. A standard function block (FB10) is provi​ded by DeltaLink for decode actions inside the PLC. The standard function block FB10 is cal​led "ENCODED", and uses SFC20 and an instance data block. The instance data block should contain the information from an encoded write. The protocol driver places the information in a special way in the encode DB.

	Encode DB
	
	

	Data byte
	Type
	Description

	DBB0
	KF
	Reserved

	DBB1
	KF
	Reserved

	DBB2
	KY
	Destination

	DBB3
	KY
	destination type

	DBB4+5
	KY
	DB no..

	DBB6+7
	KY
	address no.

	DBB8
	KY
	Bit no.

	DBB9
	KY
	Change flags

	DBB10
	KY
	Value

	DBB11
	KY
	Value

	DBB12
	KY
	Value

	DBB13
	KY
	Value


Figure F.1 Encode Data Block.

Destination the information in this byte indicates the destination of the value which should be updated.


Value

Description


M
=
Flag type.


D
=
Data block.


A
=
Output.


E
=
Input.

Destination type the information in this byte indicates the destination type of the value which should be updated.


Value

Description


F
=
Flag for DB, F, A or E.


B
=
Byte for DB, F, A or E.


W
=
Word for DB, F, A or E.


D
=
Double word, for long integer or float.

DB number The information in this byte is the number of a DB. If the destination is not D the value in this byte is irrelevant. The value is between 0 and 4095.

Address number address number of the byte, word, data word, timer or counter.  The value is between 0 and 4095.

Bit number the number of the bit in a word or a flag. If the destination type is not flag, the value is irrelevant.

Change flags For every encoded write the protocol driver writes the value 255 in this byte. Function block FB10 uses this value to detect if there is new information.

Value value may be up to longs, depending on the type of data. For flag and byte values DBB16 is used. For word values DBW10 is used. And for long integers and float DBD8 plus DBW10 is used.

FB10 ENCODED

[image: image5.png]DBLO

B0
en T Enn

ss





 Figure F.2.2 Function Block FB10.

Parameters

Instance DB
The function block needs an instance DB, specify the desired block number.

S5
Boolean to specify if S5 addressing mode is to be used. A value of TRUE means that the S5 addressing mode is used. S7 addressing mode is used when the value is FALSE. 

Appendix F. Debug Viewer

Introduction

DebugView is an application that lets you monitor debug output on your local system, or any computer on the network that you can reach via TCP/IP. It is capable of displaying both kernel-mode and Win32 debug output, so you don't need a debugger to catch the debug output your applications or device drivers generate, nor do you need to modify your applications or drivers to use non-standard debug output APIs. 

DebugView works on Windows 95, 98, Me, 2000, XP, Windows Server 2003, Windows for x64 processors and Windows Vista. 

DebugView Capture

Under Windows 95, 98, and Me DebugView will capture output from the following sources:

• Win32 OutputDebugString

• Win16 OutputDebugString

• Kernel-mode Out_Debug_String

• Kernel-mode _Debug_Printf_Service

Under Windows NT, 2000, XP, Server 2003 and Vista DebugView will capture:

• Win32 OutputDebugString

• Kernel-mode DbgPrint

• All kernel-mode variants of DbgPrint implemented in Windows XP and Server 2003

DebugView also extracts kernel-mode debug output generated before a crash from Window NT/2000/XP crash dump files if DebugView was capturing at the time of the crash.

Installation and Use

Simply execute the DebugView program file (dbgview.exe) and DebugView will immediately start capturing debug output. This is a screenshot of DebugView capturing Win32 debug output from a remote system. Note the presence of a highlighting filter.
[image: image6.png]BEE|
Ble Edt Copture Qptions Remote Help

H@ QA @=- A BT 9P M

3

[ Tine

Toobag Beine T

00000014 2 43599757

JISTO. MEMIAPY Receive. cnd - 2. cadECK - 0

00000016 250058796 JSIO: Vrite thresd rumming
00000017 327454765 JSIO: MEM ReadhndirateThresd: k = §

00000018 327477327 JSIO: MEMIT :CtlMessage: Control Type * 0

00000015 3127500713 JSIO: MEMI CTLTYPE_ORN. UNUSED

00000020 327525056  JSIO: MEHI: a>ControlBytes - 3. len * 207

00000021 327849111 JSIO: MEMI: :NURMESSAGE START len = 196

00000022 327574365 JSIO: RCVS: 40x12 V4012 xVOX00 0300 0x00 0x00 000 Ox
00000023 343998471 JSI0. MEMIAPI. Receive: cnd = 2. cadBCX = 0

00000025 4 75002495 _JSIO. NEMIAPI . Recesve: cnd » 2. cadBCX = 0

00000027 4.75067296  JSIO: Vrite thread rumming

00000028 500004104 _JSTO. MEMIAPI " Receive' cad = 2. cadECK = 0

00000030 500061820  JSIO: Write thresd rumming

00000031 § 29005423  JSIO: MEMI ReadanduriteThread: k = 7

00000032 € 29028005 JSIO: NEMI.CtlMessage: Contvol Type = 0

00000033 § 29051356 JSIO: MENI CTLTYPE_OEM. UNUSED

00000034 29075722 JSIO: MEMI: a->ConfrolBytes = 3. len = 207

00000035 529099804  JSIO: MEMI. :NUMESSAGE START len = 136

00000036 © 29124975 JSIO. ROVS. 40x12 xV40x12 V000 0x00 0x00 0x00 0x00 Ox. . =i





To run DebugView on Windows 95 you must get the WinSock2 update from Microsoft. Note that if you run DebugView on Windows NT/2K/XP you must have administrative privilege to view kernel-mode debug output. Menus, hot-keys, or toolbar buttons can be used to clear the window, save the monitored data to a file, search output, change the window font, and more. The on-line help describes all of DebugView's features. 

Appendix G. Blackbox crash handler

Introduction

BlackBox is a dll that you simply load up and then forget about. It will set a crash handler as soon as the library is loaded (in DLLMain()), and then just waits patiently for your application/driver to crash. If and/or when your application/driver crashes, instead of just displaying an error message like "Error writing to memory address 0XDEADBEEF", a nice little dialog comes up that displays the information in a fashion similar to Netscape's TalkBack, or the new error reporting dialog that pops up with the newer version of Microsoft's Internet Explorer. This dialog allows the user to then copy or save the crash data, and then email or be taken to an appropriate website where they can submit the information. This information can then be used by a programmer to have a much better idea of exactly where the problem occurred, as well as information about the machine that it crashed on.

[image: image7.png]BlackBox

g v s beendtect by Blacon

T help the development process,tis program wil by and gather as much nformation
about the crash, and the state of your machine a the time ofthe crash. This deta wil can

then be either copied 1o the clpboid or saved 10 a fed as plain text

You canthen either emai to fduto@iscal.nl and paste the nformation rto the Detaled

Descipton field

Exception Reason

s3pi_s7 EXE caused an EXCEPTION_ACCESS_VIDLATION inmode
sapi_s7 EXE ot 0018:00404DDS, sapi_read(}+0T63 byefs],
d\tscnomalis\projects\sapl_s7\src\cleapi_., Ine 1030+0003 byefs]

Regisers
000000 EBX=00ESF1DE ECX=00000002 EDX=00000002

EDI-00E 36360 EBP-00000000 ESP=013CFFF4 EIP-00000000
C52001B DS=0023 550023 ES=0023 FS=0038 GS=0000

Stack Trace

001B:00404DD3 sapi_s7.EXE. sapi_tead(}+0169 bytefs), & ecnomatis\pro
O01B:0041324E sapi_s7 EXE, Ims_MT_ThieacRead_Ini(}+0021 bytefs), [
001B:77C34243 MSVCRT.di
001B:7CA0B583 kemelz2.

Infarmatian.

State





Usage

BlackBox displays a variety of information:

· The Exception Reason

· The Registers

· The Stack Trace, a complete stack trace from where the error occured

· The machine information, such as CPU, OS version, physical memory, etc. Clicking on the "Information..." button will display this in a dialog.

· The machine state - a list of ALL the processes running at the time of the crash, and any DLLs loaded by the processes. Clicking on the "State..." button will display this in a dialog. 

As a user, you can copy the contents to the clipboard by clicking on the "Copy" button. Clicking the "Save..." button will prompt you to save the contents to a file, with the default name being of the form: "errorlog-<GMT time, dd-mm-yyyy>(<time, hh:mm:ss>).log".

Click the "Mail To..." button and an attempt will be made to execute the mailto: command on your system. Assuming a properly installed email program, it will be brought up with the appropriate email address.


















� EMBED Word.Picture.8  ���












































�{FLINK} is the working directory for the FactoryLink programs.





[image: image17.png]\g the PG/PC Interface (R4.1.6.2)

pccsss |

Access Point of Applicaton:
STONLINE  (STEF 7) B
(Standard for STEP 7)

Mode Parameter Set ised:

[EFT413 <Actives Propetes.
(Hore> Diagrostcs
TCP/IP > DEC PUI Fast Ethemel
oy
(Configurston of your Commurications
Processor CP 1413 for an Industial Ethernet
Network)
Modies
Instal

W Carcel Hep




[image: image18.png]


[image: image19.png]1

DB15

EN

1D

§6

FB15

END

DONE

ERROR

STATUS

MO.1

MW10



[image: image20.png]DB15

EN

ID

85

FB15

END

DONE

ERROR

STATUS

MO.1

MW10



[image: image21.png]DB15

EN

85

FB15

END 1

DONE |

ERROR{

STATUS ¢

MO.1

MW10



[image: image22.png]BISIMATIC NET  COML S7 -SIEMENS.TXT

File Help
Nods name: Network 0
[SIEMENS ] [erenner =]

S7 connection list

WRITE
RECEIVE

Delete

Edit $7 connection selected on left

VFD Name

Remote Addr

Local TSAP:

Remote TSAP:

FD1

Ii

[08.00.06.01.00.02

—
—

| =




[image: image23.png]Registy Editor

Registy Edt_View Help

[=[ofx]

=0 HKEY_LOCAL_MACHINE

{20 HARDWARE

{23 5AM
{2 SECURITY
=0 SOFTWARE

a
{23 Adobe
{2 Apple
{23 Amy 0. Chemavin
{2 Classes
{2 Clents
{20 Dehaink.
{2 Description
{21 DigalE quipmentCorporation
{23 Dynasolt
{2 Handberg
{20 INTEL
{20 INTERSOLY
{23 lomega Corporation
{23 Labtam
{2 Microsoft
{2 opBC
{2 Program Groups.
{20 Prospera Intemational Ltd.
@scc
{3 Secure
=0 SIEMENS
3 AuTSW
{20 SIMATIC_NET
=0 SINEC
{2 Deevices
{2 LogDevices
{2 Loghames
{3 PaSP
=3 5APLST

{20 57_TRACE_DEPTH

Name

[ Data

28] Defaut)

[cPrata s7ioe
()57 _oevice_FiLTER
(557 TRACE_DEPTH
(2557 TRACE_FILENAME
(557 TRACE_MAXFILES
(3557 TRACE_MAXLINES
(857 TRace_SeLECT
()57 TRACE_TARGET

vale not se)
“D:\Siemens b
“defaul”

“25E

\STTrace




[image: image24.png]DB16

EN

ID

85

FB16

END

DONE

ERROR7

STATUS

MO.1

MW10



[image: image25.png]DB17

Mo.0
el ERROR Mo.1
FALSE STATUS MW10

P#DB10.dbx 2.0
BYTE

10




[image: image26.png]8 Siemens API Device def
Edt View Uilties Est Help

(O]

Receive Connection Encode DB Status. Read Disable Disable Rev Disable
RECEVE 1 ]
Cancel Enter Exit Next Prev.




[image: image27.png]iemens SAPI Mailbox def (O]

Edt View Uilties Est Help

Protocol Driver
Mailbox Tag

sAP!_STMBX S

Description

‘sapi_s7 mailbox

Cancel |

Enter

| | Exit

Next

=




[image: image28.png]Edt View Uilties Est Help

(O]

Translator Max MSG E
Mailbox Tag
0xLATORMBX 5 ININTT] TOXLATOR Mailbox

d

Cancel | | Enter

Next

Prev.




[image: image29.png]iemens API Device def

(O]

Edi View Uiitiss Exst Hel
Device Name *Board Connection Comm Type Encode DB Status
[TET | cP_H1_1: PLCT P 10 conn_status[0]
Cancel Enter Exit Next Prev




[image: image30.png]iemens API Device def

(O]

Edi View Uiitiss Exst Hel
Encode DB Status Cyclic Read Disable | Write Disable Rev Disable
Count
10 conn_status[0] disable[0] disable[] [isable[2] |
Cancel Enter Exit Next Prev




[image: image31.png]Edt View Uilties Est Help

(O]

Translator Data Set Type DB Start | Length Cydlic E
Mailbox Tag Read
DataSet[0] DB 50 2 10
IOXLATORMBX S | DataSet[1] DB 50 6 2
IOXLATORMBX S | DataSet[2] DB 50 10 14
IOXLATORMBX S | DataSet[3] DB 50 10 14
IOXLATORMBX S | DataSet[] DB 50 10 14
IOXLATORMBX S | DataSet[s] DB 1 0 0
IOXLATORMBX S | DataSet[6] DB 50 30 36 d
I0XLATORMBX S | DataSet[7] DB 50 30 36
Device Name [DEVD
Cancel Enter Next Prev




[image: image32.png]BASIMATIC NET  COML S7 -TCPIP.TXT A

Fie Help
Node name: Network type
[sapi_tep TCPAP -
S7 connection list Edit 57 connection selected on left
P Hame: PLCT

VFD Name [vFD1

Bemote Addr:  [194.229.87.30

Local TSAP: [01.00 | (hexadecimal)

Remote TSAP:  [01.00 | (hexadecimal)

Delete Insert Replace Cancel




[image: image33.png]Properties - CP1413
Ethemel{MAC)Addess S7-Frotacel | Mode |

Database
7 activete 57

SAPI.S7 Database.

e

To de-/activate 57 database, lick checkbos Activale 57

Desciption

[ Cancel Standard Help




[image: image34.png]Properties - CP1413
Ethemel{MAC)Addess S7-Frotacel | Mode |

Database
7 activete 57

SAPI.S7 Database.

[CASinechsapt_s7.nt\sampleNex b

Seatch
Desciption

To de-/activate 57 database, lick checkbos Activale 57

[ Cancel Standard Help




[image: image35.png]\g the PG/PC Interface (R4.1.6.2)
pccsss |
Access Point of Application:
o G
[for CP1413  SIMATIC NET)

Mode Parameter Set ised:

[EFT413 <Actives Propetes.
Diagrostcs
TCP/IP > DEC PUI Fast Ethemel
oy
(Configurston of your Commurications
Processor CP 1413 for an Industial Ethernet
Network)
Modies
Instal

[ Cancel Help




[image: image36.png]Install/Remove Modules

Selection

411D
CFid13
CF151T{4ccton EN2216 PC
CPss1242

150 Ind. Etheret

TCP/P

i—

CHEFanid

Instaleg
s Goadt |
TCP/P > DEC POl Fast Ethemet Bo.
| —

Hestiices

[CPT#11 Industial Ethemet NDIS Netwarkboard [PLUgtPiay)

e




[image: image37.png]BASIMATIC NET  COML S7 -TCPIP.TXT A

File Help
Nods name Network 0
[evi_ton ] [tcene =]
57 connection list Edit 57 connection selected on left

P Hame: PLCT
VFD Name [vFD1

Bemote Addr:  [194.229.87.30

Local TSAP: (hexadecimal)
Remote TSAP: (hexadecimal)

Delete Insert Replace | Cangel




[image: image38.jpg]


_961237013.doc
[image: image1.png]iemens SAPI Mailbox def (O]

Edt View Uilties Est Help

Protocol Driver
Mailbox Tag

sAPIMBX

Des

Sapi

ailbox Tag

Cancel

Enter

Exit

Next

Prev.

=





 


[image: image2.png]iemens SAPI Mailbox def (O]

Edt View Uilties Est Help

Protocol Driver
Mailbox Tag

sAPIMBX

Des

Sapi

ailbox Tag

Cancel

Enter

Exit

Next

Prev.

=






_962446068.doc
[image: image1.png]DB15

EN

85

FB15

END 1

DONE |

ERROR{

STATUS ¢

MO.1

MW10







_962449536.doc
[image: image1.png]8 Siemens API Device def
Edt View Uilties Est Help

(O]

Receive Connection Encode DB Status. Read Disable Disable Rev Disable
RECEVE 1 ]
Cancel Enter Exit Next Prev.








_1007988849.doc
[image: image1.png]BASIMATIC NET  COML S7 -TCPIP.TXT A

File Help
Nods name Network 0
[evi_ton ] [tcene =]
57 connection list Edit 57 connection selected on left

P Hame: PLCT
VFD Name [vFD1

Bemote Addr:  [194.229.87.30

Local TSAP: (hexadecimal)
Remote TSAP: (hexadecimal)

Delete Insert Replace | Cangel








_962444608.doc
[image: image1.png]






_960363637.doc
[image: image1.png]iemens SAPI Mailbox def (O]

Edt View Uilties Est Help

Protocol Driver
Mailbox Tag

sAPIMBX

Des

Sapi

ailbox Tag

Cancel

Enter

Exit

Next

Prev.

=





 


_960885055.doc
[image: image1.png]Registy Editor

Registy Edt_View Help

[=[ofx]

=0 HKEY_LOCAL_MACHINE

{20 HARDWARE

{23 5AM
{2 SECURITY
=0 SOFTWARE

a
{23 Adobe
{2 Apple
{23 Amy 0. Chemavin
{2 Classes
{2 Clents
{20 Dehaink.
{2 Description
{21 DigalE quipmentCorporation
{23 Dynasolt
{2 Handberg
{20 INTEL
{20 INTERSOLY
{23 lomega Corporation
{23 Labtam
{2 Microsoft
{2 opBC
{2 Program Groups.
{20 Prospera Intemational Ltd.
@scc
{3 Secure
=0 SIEMENS
3 AuTSW
{20 SIMATIC_NET
=0 SINEC
{2 Deevices
{2 LogDevices
{2 Loghames
{3 PaSP
=3 5APLST

{20 57_TRACE_DEPTH

Name

[ Data

28] Defaut)

[cPrata s7ioe
()57 _oevice_FiLTER
(557 TRACE_DEPTH
(2557 TRACE_FILENAME
(557 TRACE_MAXFILES
(3557 TRACE_MAXLINES
(857 TRace_SeLECT
()57 TRACE_TARGET

vale not se)
“D:\Siemens b
“defaul”

“25E

\STTrace








_960971376.doc
[image: image1.png](O]
Edt Vew Uies Ext Heb
Translator Data Set Type | DB | Stat | Length E
Mailbox Tag
DS0 DB 50 0 10
IOXLATORMBX_S | DS1 DB 50 5 1
I0XLATORMBX S | DS2 DB 50 10 14
I0XLATORMBX S | DS3 DB 50 10 14
I0XLATORMBX S | DS4 DB 50 10 14
I0XLATORMBX S | DS5 DB 11 0 12
IOXLATORMBX S | DS6 DB 50 30 36 )
I0XLATORMBX S | DS7 0B 50 30 36
P —
Cancel | | Enter || B | Next Prev.








_960883986.doc
[image: image1.png]BISIMATIC NET  COML S7 -SIEMENS.TXT

File Help
Nods name: Network 0
[SIEMENS ] [erenner =]

S7 connection list

WRITE
RECEIVE

Delete

Edit $7 connection selected on left

VFD Name

Remote Addr

Local TSAP:

Remote TSAP:

FD1

Ii

[08.00.06.01.00.02

—
—

| =








_960362464.vsd

_960362792.vsd

_930602771.doc
��



RAPD







�
















_932386625.doc
��



RAPD







�
















_930602543.doc
��



RAPD







�
















