{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["IO Lith","Rekken Lith"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"IO Lith","index":0,"n_rows":283,"n_cols":5,"rows_kept":283,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["led","POSITIE",16,null,"UITGANGSKAART DIGITAAL"]
[1,"CLIT_001","DO",1,"UITSCHAKELEN AFSTANDBEDIENING"]
[2,"CLIT_002","DO",2,"INSCHAKELEN  AFSTANDBEDIENING"]
[3,"CLIT_011","DO",3,"ANNULEREN STORINGSMELDINGEN"]
[4,"CLIT_012","DO",4,"ANNULEREN STORINGEN"]
[5,"CLIT_101","DO",5,"UITSCHAKELEN HD POMP-UNIT 1"]
[6,"CLIT_102","DO",6,"UITSCHAKELEN HD POMP-UNIT 2"]
[7,"CLIT_103","DO",7,"UITSCHAKELEN HD POMP-UNIT 3"]
[8,"CLIT_104","DO",8,"UITSCHAKELEN HD POMP-UNIT 4"]
[9,"CLIT_105","DO",9,"UITSCHAKELEN HD POMP-UNIT 5"]
[10,"CLIT_106","DO",10,"UITSCHAKELEN HD POMP-UNIT 6"]
[11,"CLIT_201","DO",11,"INSCHAKELEN  HD POMP-UNIT 1"]
[12,"CLIT_202","DO",12,"INSCHAKELEN  HD POMP-UNIT 2"]
[13,"CLIT_203","DO",13,"INSCHAKELEN  HD POMP-UNIT 3"]
[14,"CLIT_204","DO",14,"INSCHAKELEN  HD POMP-UNIT 4"]
[15,"CLIT_205","DO",15,"INSCHAKELEN  HD POMP-UNIT 5"]
[16,"CLIT_206","DO",16,"INSCHAKELEN  HD POMP-UNIT 6"]
[17,"CLIT_301","DO",17,"OPENEN TRANSPORTAFSLUITER 1"]
[18,"CLIT_302","DO",18,"OPENEN TRANSPORTAFSLUITER 2"]
[19,"CLIT_311","DO",19,"STOPPEN TRANSPORTAFSLUITER 1"]
[20,"CLIT_312","DO",20,"STOPPEN TRANSPORTAFSLUITER 2"]
[21,"CLIT_321","DO",21,"SLUITEN TRANSPORTAFSLUITER 1"]
[22,"CLIT_322","DO",22,"SLUITEN TRANSPORTAFSLUITER 2"]
[23,"CLIT_401","DO",23,"UITSCHAKELEN PRODUCTIE"]
[24,"CLIT_402","DO",24,"INSCHAKELEN  PRODUCTIE"]
[25,"NC_000025","DO",25,"NC"]
[26,"NC_000026","DO",26,"NC"]
[27,"CLIT_461","DO",27,"OPENEN  VULAFSLUITER"]
[28,"CLIT_462","DO",28,"STOPPEN VULAFSLUITER"]
[29,"CLIT_463","DO",29,"SLUITEN VULAFSLUITER"]
[30,"CLIT_464","DO",30,"VULAFSLUITER NAAR REGELSTAND"]
[31,"CLIT_901","DO",31,"NC"]
[32,"CLIT_911","DO",32,"SETP. TRANSP. DRUK 1 OP LOKAAL"]
[]
["led","POSITIE",17,null,"UITGANGSKAART DIGITAAL"]
[1,"CLIT_912","DO",33,"SETP. TRANSP. DRUK 1 OP T.M."]
[2,"CLIT_931","DO",34,"SETP. TRANSP. HOEV. 1 OP LOKAAL"]
[3,"CLIT_932","DO",35,"SETP. TRANSP. HOEV. 1 OP T.M."]
[4,"CLIT_951","DO",36,"SETP. VULHOEVEELHEID OP LOKAAL"]
[5,"CLIT_952","DO",37,"SETP. VULHOEVEELHEID OP T.M."]
[6,"CLIT_961","DO",38,"SETP. VULLEIDINGDRUK OP LOKAAL"]
[7,"CLIT_962","DO",39,"SETP. VULLEIDINGDRUK OP T.M."]
[8,"CLIT_981","DO",40,"UITSCHAKELEN AFST. BED. SETPOINT"]
[9,"CLIT_982","DO",41,"INSCHAKELEN  AFST. BED. SETPOINT"]
[10,"NC_000042","DO",42,"NC"]
[11,"NC_000043","DO",43,"NC"]
[12,"NC_000044","DO",44,"NC"]
[13,"NC_000045","DO",45,"NC"]
[14,"NC_000046","DO",46,"NC"]
[15,"NC_000047","DO",47,"NC"]
[16,"C_Watchdog","DO",48,"Watchdog"]
[17,"NC_000049","DO",49,"NC"]
[18,"NC_000050","DO",50,"NC"]
[19,"NC_000051","DO",51,"NC"]
[20,"NC_000052","DO",52,"NC"]
[21,"NC_000053","DO",53,"NC"]
[22,"NC_000054","DO",54,"NC"]
[23,"NC_000055","DO",55,"NC"]
[24,"NC_000056","DO",56,"NC"]
[25,"NC_000057","DO",57,"NC"]
[26,"NC_000058","DO",58,"NC"]
[27,"NC_000059","DO",59,"NC"]
[28,"NC_000060","DO",60,"NC"]
[29,"NC_000061","DO",61,"NC"]
[30,"NC_000062","DO",62,"NC"]
[31,"NC_000063","DO",63,"NC"]
[32,"NC_000064","DO",64,"NC"]
[]
["led","POSITIE",7,null,"INGANGSKAART DIGITAAL"]
[1,"NC_100001","DI",100001]
[2,"NC_100002","DI",100002]
[3,"ALIT_003","DI",100003,"PRIMAIR STORING POMPGEBOUW 1"]
[4,"ALIT_007","DI",100004,"PRIMAIR STORING FILTERGEBOUW 1"]
[5,"NC_100005","DI",100005]
[6,"NC_100006","DI",100006]
[7,"ALIT_013","DI",100007,"SECUNDAIR STORING POMPGEBOUW 1"]
[8,"ALIT_017","DI",100008,"SECUNDAIR STORING FILTERGEBOUW 1"]
[9,"ALIT_021","DI",100009,"ACCUSPANNING TE LAAG"]
[10,"ALIT_022","DI",100010,"STORING  24 V AUTOMATEN"]
[11,"ALIT_024","DI",100011,"STORING 220 V AUTOMATEN"]
[12,"ALIT_025","DI",100012,"STORING GELIJKRICHTER"]
[13,"ALIT_031","DI",100013,"STORING DIESELGENERATOR 1"]
[14,"ALIT_034","DI",100014,"STORING VENTILATIE DIESELGENERATOR 1"]
[15,"ALIT_037","DI",100015,"KOELW. TMP. DIESELGENERATOR 1 TE LAAG"]
[16,"ALIT_041","DI",100016,"STORING GENERATORSCHAKELAAR 1"]
[17,"ALIT_051","DI",100017,"STORING TRAFOSCHAKELAAR 1"]
[18,"ALIT_061","DI",100018,"STORING RAILSYSTEEM 1"]
[19,"ALIT_080","DI",100019,"WATER OP DE VLOER"]
[20,"ALIT_081","DI",100020,"BLOKKERING HD-POMPEN BIJ W.O.V."]
[21,"ALIT_101","DI",100021,"STORING HD POMPUNIT 1"]
[22,"ALIT_102","DI",100022,"STORING HD POMPUNIT 2"]
[23,"ALIT_103","DI",100023,"STORING HD POMPUNIT 3"]
[24,"ALIT_104","DI",100024,"STORING HD POMPUNIT 4"]
[25,"ALIT_105","DI",100025,"STORING HD POMPUNIT 5"]
[26,"ALIT_106","DI",100026,"STORING HD POMPUNIT 6"]
[27,"ALIT_201","DI",100027,"STORING TRANSPORTDRUK 1 TE LAAG"]
[28,"ALIT_202","DI",100028,"STORING TRANSPORTDRUK 2 TE LAAG"]
[29,"ALIT_211","DI",100029,"STORING TRANSPORTDRUK 1 TE HOOG"]
[30,"ALIT_212","DI",100030,"STORING TRANSPORTDRUK 2 TE HOOG"]
[31,"ALIT_251","DI",100031,"STORING TRANSPORTHOEV.1 TE HOOG"]
[32,"ALIT_281","DI",100032,"STORING FREQUENTIEREGELAAR 1"]
[]
["led","POSITIE",8,null,"INGANGSKAART DIGITAAL"]
[1,"ALIT_291","DI",100033,"STORING HD-AUTOMAAT 1"]
[2,"ALIT_301","DI",100034,"STORING TRANSPORTAFSLUITER 1"]
[3,"ALIT_302","DI",100035,"STORING TRANSPORTAFSLUITER 2"]
[4,"ALIT_401","DI",100036,"STORING REINWATERKELDER TE LAAG"]
[5,"ALIT_402","DI",100037,"STORING REINWATERKELDER TE HOOG"]
[6,"ALIT_403","DI",100038,"BLOKKERING HOGEDRUKPOMPEN OP RWK"]
[7,"ALIT_411","DI",100039,"STORING POMPPUTTEN 1"]
[8,"ALIT_431","DI",100040,"STORING HOOG NIVEAU FILTERS 1"]
[9,"ALIT_441","DI",100041,"STORING PROCESLUCHTVENTILATIE 1"]
[10,"ALIT_501","DI",100042,"STORING PRODUCTIE 1"]
[11,"ALIT_511","DI",100043,"STORING PROCUCTIEHOEVEELHEID 1 TE LAAG"]
[12,"ALIT_514","DI",100044,"STORING KELDERVULLING"]
[13,"ALIT_521","DI",100045,"STORING RUWWATERHOEVEELHEID 1 TE LAAG"]
[14,"ALIT_541","DI",100046,"STORING SPOELAUTOMAAT 1"]
[15,"ALIT_551","DI",100047,"STORING STUURLUCHTDRUK 1 TE LAAG"]
[16,"NC_100048","DI",100048,"NC"]
[17,"ALIT_581","DI",100049,"STORING TUSSENKELDER TE LAAG"]
[18,"ALIT_582","DI",100050,"STORING TUSSENKELDER TE HOOG"]
[19,"ALIT_701","DI",100051,"STORING FILTER 1"]
[20,"ALIT_702","DI",100052,"STORING FILTER 2"]
[21,"ALIT_703","DI",100053,"STORING FILTER 3"]
[22,"ALIT_704","DI",100054,"STORING FILTER 4"]
[23,"ALIT_705","DI",100055,"STORING FILTER 5"]
[24,"ALIT_706","DI",100056,"STORING FILTER 6"]
[25,"ALIT_707","DI",100057,"STORING FILTER 7"]
[26,"ALIT_708","DI",100058,"STORING FILTER 8"]
[27,"ALIT_741","DI",100059,"STORING VULAFSLUITER"]
[28,"ALIT_742","DI",100060,"STORING VULLEIDINGDRUK TE LAAG"]
[29,"ALIT_811","DI",100061,"STORING METING BUFFERKELDER 1 OF 2"]
[30,"ALIT_861","DI",100062,"STORING METING REINWATERKELDER 1 OF 2"]
[31,"NC_100063","DI",100063,"NC"]
[32,"NC_100064","DI",100064,"NC"]
[]
["led","POSITIE",9,null,"INGANGSKAART DIGITAAL"]
[1,"ALIT_882","DI",100065,"NC"]
[2,"ALIT_891","DI",100066,"NC"]
[3,"ALIT_901","DI",100067,"STORING UPS"]
[4,"ALIT_941","DI",100068,"STORING INBRAAKCENTRALE"]
[5,"ALIT_942","DI",100069,"STORING HERHAALD KIEZEN"]
[6,"ILIT_001","DI",100070,"AFSTANDBEDIENING UIT"]
[7,"ILIT_002","DI",100071,"AFSTANDBEDIENING IN"]
[8,"ILIT_011","DI",100072,"NETWACHTER GENERATOR 1 UIT"]
[9,"ILIT_012","DI",100073,"NETWACHTER GENERATOR 1 IN"]
[10,"ILIT_041","DI",100074,"NETWACHTER TRAFO 1 UIT"]
[11,"ILIT_042","DI",100075,"NETWACHTER TRAFO 1 IN"]
[12,"ILIT_070","DI",100076,"INBRAAKCENTRALE UITGESCHAKELD"]
[13,"ILIT_071","DI",100077,"INBRAAK GEBOUWEN"]
[14,"ILIT_074","DI",100078,"INBRAAKCENTRALE INGESCHAKELD"]
[15,"ILIT_076","DI",100079,"INBRAAK SCHAKELGEBOUWEN"]
[16,"ILIT_077","DI",100080,"INBRAAK REINWATERKELDER(S)"]
[17,"ILIT_078","DI",100081,"INBRAAK PUT(TEN)"]
[18,"ILIT_091","DI",100082,"STORINGSMELDING OP DAG"]
[19,"ILIT_092","DI",100083,"NC"]
[20,"ILIT_093","DI",100084,"STORINGSMELDING OP A.T.M."]
[21,"ILIT_094","DI",100085,"NC"]
[22,"ILIT_101","DI",100086,"HD POMP-UNIT 1 UIT"]
[23,"ILIT_102","DI",100087,"HD POMP-UNIT 2 UIT"]
[24,"ILIT_103","DI",100088,"HD POMP-UNIT 3 UIT"]
[25,"ILIT_104","DI",100089,"HD POMP-UNIT 4 UIT"]
[26,"ILIT_105","DI",100090,"HD POMP-UNIT 5 UIT"]
[27,"ILIT_106","DI",100091,"HD POMP-UNIT 6 UIT"]
[28,"ILIT_201","DI",100092,"HD POMP-UNIT 1 IN"]
[29,"ILIT_202","DI",100093,"HD POMP-UNIT 2 IN"]
[30,"ILIT_203","DI",100094,"HD POMP-UNIT 3 IN"]
[31,"ILIT_204","DI",100095,"HD POMP-UNIT 4 IN"]
[32,"ILIT_205","DI",100096,"HD POMP-UNIT 5 IN"]
[]
["led","POSITIE",12,null,"INGANGSKAART DIGITAAL"]
[1,"ILIT_206","DI",100097,"HD POMP-UNIT 6 IN"]
[2,"ILIT_301","DI",100098,"TRANSPORTAFSLUITER 1 OPEN"]
[3,"ILIT_302","DI",100099,"TRANSPORTAFSLUITER 2 OPEN"]
[4,"ILIT_311","DI",100100,"TRANSPORTAFSLUITER 1 STOP"]
[5,"ILIT_312","DI",100101,"TRANSPORTAFSLUITER 2 STOP"]
[6,"ILIT_321","DI",100102,"TRANSPORTAFSLUITER 1 DICHT"]
[7,"ILIT_322","DI",100103,"TRANSPORTAFSLUITER 2 DICHT"]
[8,"ILIT_401","DI",100104,"PRODUKTIE UITGESCHAKELD"]
[9,"ILIT_402","DI",100105,"PRODUKTIE INGESCHAKELD"]
[10,"ILIT_411","DI",100106,"MAXIMALE PRODUKTIE UIT"]
[11,"ILIT_412","DI",100107,"MAXIMALE PRODUKTIE IN"]
[12,"ILIT_461","DI",100108,"VULAFSLUITER OPEN"]
[13,"ILIT_462","DI",100109,"VULAFSLUITER STOP"]
[14,"ILIT_463","DI",100110,"VULAFSLUITER DICHT"]
[15,"ILIT_464","DI",100111,"VULAFSLUITER REGELSTAND"]
[16,"ILIT_501","DI",100112,"LOOPTIJD FILTER 1 AKTIEF"]
[17,"ILIT_502","DI",100113,"LOOPTIJD FILTER 2 AKTIEF"]
[18,"ILIT_503","DI",100114,"LOOPTIJD FILTER 3 AKTIEF"]
[19,"ILIT_504","DI",100115,"LOOPTIJD FILTER 4 AKTIEF"]
[20,"ILIT_505","DI",100116,"LOOPTIJD FILTER 5 AKTIEF"]
[21,"ILIT_506","DI",100117,"LOOPTIJD FILTER 6 AKTIEF"]
[22,"ILIT_507","DI",100118,"LOOPTIJD FILTER 7 AKTIEF"]
[23,"ILIT_508","DI",100119,"LOOPTIJD FILTER 8 AKTIEF"]
[24,"ILIT_911","DI",100120,"SETP. TRANSP. DRUK  1 OP LOKAAL"]
[25,"ILIT_912","DI",100121,"SETP. TRANSP. DRUK  1 OP T.M."]
[26,"ILIT_931","DI",100122,"SETP. TRANSP. HOEV. 1 OP LOKAAL"]
[27,"ILIT_932","DI",100123,"SETP. TRANSP. HOEV. 1 OP T.M."]
[28,"ILIT_951","DI",100124,"SETP. VULHOEVEELHEID OP LOKAAL"]
[29,"ILIT_952","DI",100125,"SETP. VULHOEVEELHEID OP T.M."]
[30,"ILIT_961","DI",100126,"SETP. VULLEIDINGDRUK OP LOKAAL"]
[31,"ILIT_962","DI",100127,"SETP. VULLEIDINGDRUK OP T.M."]
[32,"ILIT_981","DI",100128,"AFSTANDSBEDIENING SETPOINT UIT"]
[]
["led","POSITIE",13,null,"INGANGSKAART DIGITAAL"]
[1,"ILIT_982","DI",100129,"AFSTANDSBEDIENING SETPOINT IN"]
[2,"NC_100130","DI",100130,"NC"]
[3,"NC_100131","DI",100131,"NC"]
[4,"NC_100132","DI",100132,"NC"]
[5,"NC_100133","DI",100133,"NC"]
[6,"RETCL","DI",100134,"RESET TERREINCLAXON"]
[7,"ANNULEER","DI",100135,"ANNULEER STORING VANUIT GEBOUW 1"]
[8,"SEBW1_2","DI",100136,"NC"]
[9,"NC_100137","DI",100137,"FILTRAATPOMP1 IN"]
[10,"NC_100138","DI",100138,"FILTRAATPOMP2 IN"]
[11,"NC_100139","DI",100139,"FILTRAATPOMP3 IN"]
[12,"NC_100140","DI",100140,"STORING FILTRAATPOMP 1"]
[13,"NC_100141","DI",100141,"STORING FILTRAATPOMP 2"]
[14,"NC_100142","DI",100142,"STORING FILTRAATPOMP 3"]
[15,"NC_100143","DI",100143,"NC"]
[16,"NC_100144","DI",100144,"NC"]
[17,"TLIT_101","DI",100145,"TRANSPORT 1 POSITIEF"]
[18,"TLIT_102","DI",100146,"TRANSPORT 2 POSITIEF"]
[19,"TLIT_411","DI",100147,"RUWWATER 1"]
[20,"TLIT_421","DI",100148,"SPOELWATER 1"]
[21,"TLIT_431","DI",100149,"PRODUCTIE 1"]
[22,"TLIT_432","DI",100150,"PRODUCTIE 2"]
[23,"TLIT_434","DI",100151,"VULHOEVEELHEID/INNAMEHOEVEELHEID"]
[24,"TLIT_451","DI",100152,"INFILTRATIEWATER 1"]
[25,"TLIT_501","DI",100153,"FILTERLOOPTIJD FILTER 1"]
[26,"TLIT_502","DI",100154,"FILTERLOOPTIJD FILTER 2"]
[27,"TLIT_503","DI",100155,"FILTERLOOPTIJD FILTER 3"]
[28,"TLIT_504","DI",100156,"FILTERLOOPTIJD FILTER 4"]
[29,"TLIT_505","DI",100157,"FILTERLOOPTIJD FILTER 5"]
[30,"TLIT_506","DI",100158,"FILTERLOOPTIJD FILTER 6"]
[31,"TLIT_507","DI",100159,"FILTERLOOPTIJD FILTER 7"]
[32,"TLIT_508","DI",100160,"FILTERLOOPTIJD FILTER 8"]
[]
[null,"POSITIE",4,null,"INGANGSKAART ANALOOG"]
[null,"MLIT_001I","AI",300001,"TRANSPORTDRUK 1"]
[null,"MLIT_002I","AI",300002,"TRANSPORTDRUK 2"]
[null,"MLIT_010I","AI",300003,"VULLEIDINGDRUK"]
[null,"MLIT_101I","AI",300004,"TRANSPORT 1 POSITIEF"]
[null,"MLIT_102I","AI",300005,"TRANSPORT 2 POSITIEF"]
[null,"MLIT_150I","AI",300006,"TRANSPORT TOTAAL"]
[null,"MLIT_301I","AI",300007,"STAND TRANSPORTAFLSUITER 1"]
[null,"MLIT_302I","AI",300008,"STAND TRANSPORTAFSLUITER 2"]
[null,"MLIT_310I","AI",300009,"STAND VULAFSLUITER"]
[null,"MLIT_401I","AI",300010,"INHOUD REINWATERKELDER"]
[null,"MLIT_402I","AI",300011,"INHOUD TUSSENKELDER"]
[null,"MLIT_410I","AI",300012,"RUWWATER TOTAAL"]
[null,"MLIT_411I","AI",300013,"RUWWATER 1"]
[null,"MLIT_420I","AI",300014,"SPOELWATER TOTAAL"]
[null,"MLIT_421I","AI",300015,"SPOELWATER 1"]
[null,"MLIT_430I","AI",300016,"PRODUCTIE TOTAAL"]
[]
[null,"POSITIE",5,null,"INGANGSKAART ANALOOG"]
[null,"MLIT_431I","AI",300018,"PRODUCTIE 1"]
[null,"MLIT_432I","AI",300019,"PRODUCTIE 2"]
[null,"MLIT_434I","AI",300020,"VULLEN REINWATERKELDER"]
[null,"NC_300021I","AI",300021,"NC"]
[null,"NC_300022I","AI",300022,"NC"]
[null,"NC_300023I","AI",300023,"NC"]
[null,"NC_300024I","AI",300024,"NC"]
[null,"NC_300025I","AI",300025,"NC"]
[null,"NC_300026I","AI",300026,"NC"]
[null,"NC_300027I","AI",300027,"NC"]
[null,"NC_300028I","AI",300028,"NC"]
[null,"NC_300029I","AI",300029,"NC"]
[null,"NC_300030I","AI",300030,"NC"]
[null,"NC_300031I","AI",300031,"NC"]
[null,"NC_300032I","AI",300032,"NC"]
[null,"NC_300033I","AI",300033,"NC"]
[]
[null,"POSITIE",6,null,"UITGANGSKAART ANALOOG"]
[null,"SLIT_101U","DO",400001,"GEWENSTE TRANSPORTDRUK 1"]
[null,"SLIT_104U","DO",400002,"GEWENSTE TRANSPORTHOEVEELHEID 1"]
[null,"SLIT_110U","DO",400003,"GEWENSTE VULLEIDINGDRUK"]
[null,"SLIT_410U","DO",400004,"GEWENSTE VULHOEVEELHEID"]
[null,"NC_400005U","DO",400005,"NC"]
[null,"NC_400006U","DO",400006,"NC"]
[null,"NC_400007U","DO",400007,"NC"]
[null,"NC_400008U","DO",400008,"NC"]

{"sheet":"Rekken Lith","index":1,"n_rows":5,"n_cols":25,"rows_kept":5,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,null,null,"Basisrek Quantum 140xbp01000",{"$nulls":11},"Uitbreidingsrek Quantum 140xbp01000"]
[]
[null,null,null,1,2,3,4,5,6,7,8,9,10,null,null,11,12,13,14,15,16,17,18,19,20]
[null,null,null,"140CPS21400","140CPU11303","140NOE77111","140ACI04000","140ACI04000","140ACO13000","140DDI35300","140DDI35300","140DDI35300",null,null,null,"140CRA21120","140DDI35300","140DDI35300",null,null,"140DDO35300","140DDO35300"]