FactoryLink Valmet Damaticx CIS Protocol Driver

for

FactoryLink 7.5.x

VALMET

Version 2.0

Printed: Monday, July 20, 2009

Valmet protocol driver

The VALMET protocol driver is a FactoryLink task, which supports communication with the Valmet Damatic computer and it’s CIS interface. The driver is part of a FactoryLink system, which can be a single system or a redundant system. The driver communicates with one or more Valmet Damatic systems using a serial port for every device, or using a ethernet to serial switch. The protocol used is the Valmet Damatic Classic protocol.

FactoryLink is a registrated trademark of UGS, Richardson Texas USA.

RLD Automation

Van Sonsbeeckstraat 11

5344 JB Oss

The Netherlands

tel. +31(0) 412 655 990

fax +31(0) 412 655 991

e-mail : support@rldautomation.eu

Version

| Date | Version | State and changes |
| --- | --- | --- |
| 1994 | 1.0 | Build for FL660 |
| June-2009 | 2.0 | Conversion driver to FL751, use of Ethernet serial switch added. |

Table of Contents

Valmet protocol driver	2

Version	3

1	Introduction	6

1.1	VALMET Protocol driver	6

1.2	Scope of this document	6

1.3	References	6

2	Driver principle	8

2.1	The IO-translator RAP Driver principle	8

2.1.1	FactoryLink domain selection	8

2.2	FactoryLink task definition	9

2.3	Devices	9

2.4	Communication functions	9

2.5	Datasets	10

2.6	Block read	10

2.7	Multithreading of the driver	10

31.	 Installation	13

3.1	System requirements	13

3.2	VALMET driver installation	13

3.3	Installation of the serial port	15

4	VALMET driver configuration	17

4.1	FactoryLink task configuration	17

4.2	Run time manager configuration	17

4.2.1	Program arguments	18

4.3	INI-file	18

4.4	FactoryLink domain selection	19

4.5	Valmet Damatic Classic Tag Address Format	19

4.6	Configuration tables	20

4.6.1	Valmet Mailbox definition	20

4.6.2	Valmet translator definition	21

4.6.3	Valmet Device definition	22

4.6.4	Valmet Dataset definition	24

4.7	Valmet Set definition	26

4.7.1	Additional remarks	28

5	Valmet protocol driver error codes	31

6	Valmet protocol driver  error messages	35

This page is left blank intentionally.

# Introduction

## VALMET Protocol driver

The VALMET protocol driver is a FactoryLink task, which supports communication with the Valmet Damatic computer and it’s CIS interface. The driver is part of a FactoryLink system, which can be a single system or a redundant system. The driver communicates with one or more Valmet Damatic systems using a serial port for every device, or using a ethernet to serial switch. The protocol used is the Valmet Damatic Classic protocol.

This manual is intended for use by a technician who is familiar with the FactoryLink software. Covered in this manual are the principles of operation, installation and configuration of the software. Included in the shipment is a demo-application, which can be used as an example of how to implement the features in your FactoryLink application.

## Scope of this document

Please check the package you received with the checklist below. Should there be an item missing contact RLD Automation to correct the problem. There is a limit of 90 days after shipment to report problems!

This package includes the following:

A VALMET protocol driver build contained on a CD-ROM or diskette(s).

This manual.

You should also have:

A MCI based translator e.g. the IO-Translator.

The correct hardware and software for the serial port, or Ethernet to serial switdh on your platform.

Honeywell, Siemens, Pilz, Symadyn or Texas Instruments PLC with ethernet communication board and software to program both the CPU and the CP boards.

A serial connection between a Valmet Damatic system and the FactoryLink system, or an ethernet-network with at least both a Valmet Damatic system and the FactoryLink system connected to it.

## References

| [CIS] | DAMATIC Automation System, Process Control Computer Connection |
| --- | --- |
| [FL7_CONFIG] | FactoryLink 7.x.y Task Configuration Reference Guide |
| [PNI_ESPORT] | FPassport Networks, Ethernet Serial Server Users Manual |

This page is left blank intentionally.

# Driver principle

## The IO-translator RAP Driver principle

RAPD stands for Rapid Application Protocol Driver. The RAPD principle was adopted so that protocol drivers can be easily and rapidly configured for a FactoryLink application. RAPD is based on the Mailbox Communication Interface standard or MCI, which defines how a protocol driver task communicates with an I/O Translator task. The RAPD system consists of a protocol driver that communicates with external devices (RTUS, PLC’s, etc.) and a translator that controls data storage (going to and coming from a protocol driver) in the FactoryLink real-time database. All data collected by the protocol driver is referenced as contiguous blocks or ranges within the device. This enables communication between the driver and a device to be very efficient. All data is referenced between the driver and the translator in terms of datasets. Datasets, described in the next section, define memory regions or locations of data within a device.

Please check the package you received with the checklist below. Should there be an item missing contact DeltaLink bv to correct the problem. There is a limit of 90 days after shipment to report problems!

Figure 2.1 The RAPD principle.

The protocol driver and the I/O Translator communicate with one another through FactoryLink mailbox tags, according to the MCI standard. Every task (translator and protocol driver) has its own mailbox, so for full communication between a translator and a protocol driver a mailbox database element for every task has to be defined. The MCI standard is especially designed for the following situation. To use one translator and several protocol drivers. For example the translator together with the ISO-TP4 driver and the Modbus Plus protocol driver. Aside from storage duties, the translator provides data conversions (i.e. analog, IEEE conversions, etc.) for I/O data to/from a protocol driver.

### FactoryLink domain selection

The standard domain for the VALMET driver is the SHARED domain. The protocol driver communicates with a dedicated piece of hardware, therefore only one task should be able to access the hardware. If only one

Figure 2.2 Domain selection for the driver.

program  accesses the hardware, the task should be located in the shared domain and therefore started by the shared runtime-manager.

Important: The protocol driver and the translator must be in the same domain (either SHARED or USER).

## FactoryLink task definition

The protocol driver must, with the FactoryLink Configuration Explorer (FLCE) or the FactoryLink Configuration Manager (FLCM),  be entered in the System Configuration table. An entry of an existing task which will not be used at run-time can be overwritten or a new entry can be created with (as a minimum) the following data:

Task Name	Description   ....   				Executable File

VALMET	VALMET Protocol Driver			bin/valmet

The Task Name and name of the executable file must be filled in as shown above, the FactoryLink kernel uses these entries to start the driver, and to confirm that the driver registers correctly to the FactoryLink kernel.

Figure 2.3 Task definition of the VALMET driver in the configuration explorer.

Important: The protocol driver needs two entries in the system configuration panel, one defined as in the figure above, and one ‘free’ (or empty) task definition. If the driver can not find a free task definition when starting, the driver task will exit with an error. Practically this means: there must be less then 31 task configured in the FactoryLink system configuration table.

## Devices

Every Valmet Damatic Computer connected to the driver via network or serial cable is called a device, this term is defined in the MCI standard as a logical external device. A Valmet Damatic Computer is called a device in the FactoryLink application and has a logical name (only used in the application configuration). A serial connection is defined by the COM port used by the device, using a serial connection over TCP/IP the device is identified by the IP adres of the Ethernet-Serial switch.

## Communication functions

Data exchange between a FactoryLink workstation and a Valmet Damatic Computer is performed by using the read- and write-services of the CIS interface. The protocol driver task uses the read-service to read (or fetch) data from the Valmet Damatic Computer, and it uses the write-service to write data to the Valmet Damatic Computer. Both actions are always initiated by the driver task.

The CIS interface supports different types of read and write services, the ones supported are described in the next paragraphs. In the table below are all the possible services listed together with the information if they are supported or not.

| Protocol | Read/Write Service | Supported |
| --- | --- | --- |
| CIS interface | Block read | Yes |
|  | Block write | No |
|  | Exception write | No |
|  | Encoded write | No |
|  | Unsolicited Receive | No |

## Datasets

Data exchange is, according to the definitions stated in the MCI standard, is based upon datasets. A dataset is a contiguous area, such as a register or memory location, of data in the external device. All datasets are defined as digital tags. The protocol driver defines all specifics, such as data type about datasets, starting address, or length, while the IOX task references the dataset by tag name for read/write operations. When the IOX task initiates a trigger on a dataset, the MCI system notifies the protocol driver that an event has occurred on that dataset. The event notification, in turn, causes a protocol specific message to be generated and sent to an external device. The scenario works in reverse when the protocol driver receives unsolicited data from a device.

| Dataset | Maps to external device |
| --- | --- |
| Referenced by dataset control tag | Memory location, defined by area type, start address, and length |
| Tag 1 | Address: n |
| Tag 2 | Address: n + 1 |
| Tag 3 | Address: n + 2 |
| Tag 4 | Address: n + 3 |
| Tag x | Address: n + m |

A dataset can be read or written to with one command or trigger. With the exception of actions on the complete dataset, most protocol drivers are capable of addressing specific elements or a group of elements in the dataset. How these actions are performed depends on the size of a basic element in the dataset, which can be bit, byte, word, or long, depending on the data area in the device or the communication protocol.

## Block read

The block read commands are performed on a contiguous block of data in the external device, specified by datasets. The FactoryLink station initiates these commands. The FactoryLink application developer configures digital triggers for the IO-translator task to start the read commands. Data received from a device as a result of a read request is stored in FactoryLink tags.

## Multithreading of the driver

The VALMET driver is a high performance RAP driver, for speed considerations the driver is build as a multi-threaded task. On start-up there is initially one thread active, this thread is the ‘main’ thread, first it will load the configuration defined with the FactoryLink Configuration Explorer. In the configuration are all the device definitions found, next the protocol driver starts a thread for every device or PLC. One thread for every device is needed to perform the ‘read’ commands, a second thread executes all the ‘write’ commands and the third thread waits for unsolicited receives. In combination with MCI the first two threads will wait for any read or write command to occur. If there is a command it is immediately executed and the response is send to the I/O translator.

An additional thread, the listen thread, is started by the driver, this thread waits for incoming connection requests from devices, this thread only accept connection requests from devices supporting the unsolicited receive. The driver initiates connection requests for the read and write functionality.

The total number of threads for the device will be: 1 * number of devices + 1. The extra thread is the main thread, responsible for dispatching the read and write commands from the I/O translator to every read thread of a device.

The logical order of starting and creating threads is the following:

- Task is started, one thread present. Configuration data is loaded, among it are the device definitions.

- For every device a thread for the read command is started (MCI).

This page is left blank intentionally.

# Installation

## System requirements

The VALMET driver will install and run on any IBM PC or PC-compatible computer equipped with:

A processor equivalent to an Intel 80486 or later. RLD Automation recommends at least an Intel Pentium-class or compatible processor.

A CD-ROM.

At least 5 MB of free hard disk space.

Microsoft Windows XP/2003, with at least service pack 1 installed.

SIEMENS FactoryLink 7.5.0.

## VALMET driver installation

The main objective of the VALMET driver installation is copying a group of files from the installation media to your computer system. In this group all the files related to the FactoryLink environment are copied to your FactoryLink system directory (normally set by the ‘FLINK’ environment variable), including both the runtime and configuration options.

To start the installation procedure: locate the ‘setup.exe’ file on the installation media, and execute the setup utility.

Figure 3.1. Setup the application (large icon view).

After starting the setup, some questions have to be answered, the most important one is where your FactoryLink system directory is located. The setup assumes that the environment variable %FLINK% is correct, but gives you the opportunity to change the directory to install to. Most steps of the installation process are presented in the following figures.

Figure 3.2. The welcome wizard panel.

The first screen displayed is the ‘Welcome’ screen, click ‘Next >’ to continue. The next panel of the setup wizard displays the VALMET driver end-user license agreement. Read this agreement carefully. If you install the VALMET driver you agree to abide by the terms of the license.

If you do not agree to the license terms, click ‘I do not accept the agreement’ folowed by ‘Cancel’. Setup will quit immediately. Otherwise, click ‘I accept the agreement’ followed by ‘Next >’ to continue. The next screen will list the minimum requirements for your system needed by the VALMET driver. It also explains how to choose the program location in the next screen, press ‘Next >’ when you are ready.

Figure 3.3. The software license agreement.	Figure 3.4. Additional informaton.

Use the browse window to specify a directory for the FactoryLink system files, in case the one selected by the set-up wizard is not the one where you want to install this FactoryLink driver.

Next select the components you wish to install, the VALMET driver has three components. First the driver itself this component can not be deselected, it is always installed. The optional components are the manual in pdf-format and support files for debugging purposes. The last option includes the program ‘debug viewer’ from sysinternals.

Figure 3.5. Select the destination directory.	Figure 3.6. Select the components to install.

Figure 3.7. Ready to install the application.	Figure 3.8. Installation progress.

Figure 3.9. Installation is completed.

You need to confirm your settings and requirements, before the actual installation process is started. After completion of the installation process, the last page of the wizard is shown, and pressing the ‘Finish’ button closes the setup window.

## Installation of the serial port

It is necessary to have a serial port on your system which can be used by the protocol driver for communicating with the Valmet Damatic CIS system(s). Refer to the manual(s) of your system for installing/setting up a serial port. Make sure everything is installed correctly, and additional device drivers, when needed, are loaded. Connect the serial port to the Valmet Damatic CIS system(s), connector layouts are described in the manuals for your system and the Valmet system. Refer to reference [CIS] for information about setting the serial communication parameters used by the Valmet Damatic driver.

This page is left blank intentionally.

# VALMET driver configuration

## FactoryLink task configuration

The configuration of the VALMET driver consists of three main parts, two of these parts need some configuration, the third part has already a default configuration. This default configuration will in most cases suit the needs of every application. The configuration main parts are: Run time manager configuration, VALMET driver and IO-translator table configuration, the third part is the INI-file of the driver.

The first (Run time manager configuration) and the second (driver table configuration) configuration, are normally done with the configuration explorer (FLCE), and involves changing or adding settings in configuration tables. Third part of the configuration is the task’s INI-file, a default file is already supplied during installation, changes in this file influences your system, not only the application. The file is located in your FactoryLink system directory (%FLBIN%), and not part of an application.

Note: The VALMET driver does not need an ini-file, there is even not one installed on your FactoryLink system.

Figure 4.1 VALMET driver configuration.

## Run time manager configuration

In order to activate the VALMET driver as a FactoryLink task it needs some configuration in the ‘system configuration’ panel of the FactoryLink Configuration Explorer.

Figure 4.2 FactoryLink task configuration.

The required settings for the VALMET driver are its task name and executable name, the last one is not visible in the figure above, but can be reached by panning through the configuration row. The following settings apply:

| Task Name = VALMET Executable File = bin/valmet Figure 4.3 VALMET task definition in the configuration explorer. |  |
| --- | --- |

Important: The protocol driver needs two entries in the system configuration panel, one defined as in the figure above, and one ‘free’ (or empty) task definition. If the driver can not find a free task definition when starting, the driver task will exit with an error. Practically this means: there must be less then 31 tasks configured in the FactoryLink system configuration table.

### Program arguments

| -LSn | Local Station id with number n, needed if the protocol driver and IO-translator reside on different nodes (or FactoryLink workstations). This must be an unique (station) number for the network. Two MCI tasks (the IOX task and a protocol driver) can run on different computers communicating with one another. Because the two computers can differ in data direction (different platforms), MCI supplies information specifying where the dataset came from and what kind of data orientation it has. The station identification is a unique number of the host station on the LAN. The user must assign this number and keep it unique over the LAN. The station identification can be passed to the driver task as a program argument. If tasks are to support communications over a LAN, some information must be exchanged between the tasks before they can begin communications. The tasks are probably running on separate nodes in two different FactoryLink applications, which means all tag ids are most likely not the same on both systems. MCI uses the dataset control tag for identification of the dataset, exchanging the tag-ids between two systems does not always result in identification of the same tag!. The –LS option tells the driver to use the tag-name instead of the id to identify the dataset control tag. The –LS option accepts environment variables for the n argument, the name of the environment variable must be enclosed in curly brackets, eg {FLSTATION}, where the environment variable FLSTATION is defined as a number. |
| --- | --- |
| -dn | Debug option, the level of debug information is set with the number n. The range of this number is from 1 until 9. If no number is specified the default level will be 1. The debug output will be visible in the ‘window’ of the protocol driver, that of the run time manager. |
| -ln | Same as the previous option, difference is the output device. For this option an ASCII log file is generated, being the file: {FLAPP}/{FLNAME}/{FLDOMAIN}/log/valmet.log |
| -vn | Same as the previous option, difference is the output device. For this option the output is send to the default debug-viewer on the system. If no debug-viewer is present or active on the system, the ‘SysInternals’ program ‘dbgview.exe’ can be used to monitor the debug output (www.sysinternals.com). This program can be installed as an option to the protocol driver. |
| -mn | Internal buffersize for every thread, the buffersize n is in Kbytes. |

## INI-file

The VALMET driver does NOT use an INI-file.

## FactoryLink domain selection

The standard domain for the Valmet Damatic protocol driver is the SHARED domain. The protocol driver communicates with a dedicated piece of hardware, there fore only one task should be able to access the hardware. If only one program accesses the hardware, the task should be located in the shared domain and therefore started by the shared runtime-manager.

Important: The protocol driver and the translator must be in the same domain (either SHARED or USER).

Figure 4.4 Standard domain selection.

## Valmet Damatic Classic Tag Address Format

Internally, the Valmet GCU addresses its points by a combination of Bus Number (1-15), Process Station’s Number (1-14), Block (0-7), Signal Group (0-3) and Signal Number (0-3).

Figure 4.5  Classic tag address format.

## Configuration tables

The configuration tables for the VALMET driver can be accessed with the FactoryLink Configuration explorer. For general information about entering data in FactoryLink configuration tables refer to the FactoryLink  Manual. In the Configuration Explorer select ‘Device Interfaces’.

Figure 4.6. FactoryLink Configuration explorer.

A table entry appears: ‘VALMET Protocol Driver. This entry gives access to the configuration tables, three tables are present, ‘VALMET Device definition’, ‘VALMET Translator Definition’ and ‘VALMET Mailbox D’. The third table needs only one row to configure the mailbox used by the protocol driver. The second table defines all the translator used by the protocol driver, the configuration defaults to one row: the mailbox tag used by the IO-translator. The first table  configures all the devices (PLC’s) that will be present in the network, a sub table defines the datasets for every (selected) device.

Note: For general information about entering data in FactoryLink configuration tables, refer to the FactoryLink Fundamentals Manual.

### Valmet Mailbox definition

The ‘VALMET Driver Definition’ panel is used to define global settings for the driver. For these global settings only one record or row is needed, if you define more then one row, the driver will ignore the second and following rows. The first row however is required, an empty table will generate a task error and cause the driver to stop. The field ‘Protocol Driver Mailbox Tag’ is required, without a mailbox the drive is unable to function.

Figure 4.7. Configuration panel VALMET mailbox definition.

Enable Driver

Tag name of a digital tag, the value of this tag determines if the driver is enable or disabled. A disabled driver does not communicatie with the Valmet device. This field is optional and left empty, the driver is enabled and will function normal. A tag value ON enables the driver, the driver is disabled with a taga value OFF.

| entry | Optional |
| --- | --- |
| entry type | Tag name, tag type: DIGITAL |

Protocol Driver Mailbox Tag

Tag name of the Valmet protocol mailbox element that the developer defines, to be referenced by a IO translator task (N.B. MCI must be supported by the IO translator task). The IO translator task uses this mailbox to send requests to the Valmet protocol driver.

| entry | Required |
| --- | --- |
| entry type | Tag name, tag type: MAILBOX |

### Valmet translator definition

From the display of all the panels, select the DeltaLink Valmet Decoder definition panel.

Figure 4.8. Configuration panel VALMET translator definition.

The  DeltaLink Valmet decoder definition panel allows the user to specify one or more decoder(s). Every Mailbox Tag specifies a different decoder. Only one Mailbox Tag, for every decoder, is needed for full performance of MCI. Specify the following information.

Translator Mailbox Tag

Tag name of a translator mailbox element, to be referenced by the VALMET protocol driver (N.B. MCI must be supported by the translator task). The translator task uses this mailbox to receive data from the VALMET protocol driver.

| entry | Required |
| --- | --- |
| entry type | Tag name, tag type: MAILBOX |

Max MSG

The maximum number of requests for the protocol driver, which can be queued in the mailbox tag. Recommended is a value of 100 messages. The number of messages is limited by the size of an integer value (9999), and practically by the amount of available memory. The memory needed for a request depends on the size of the configured datasets.

| entry | Required |
| --- | --- |
| entry type | Numerical value, 1..9999 |
| default | If not configured the value defaults to 100 messages |

### Valmet Device definition

The Valmet Device definition panel allows the user to specify logical devices for the communication. Each logical device uses exclusively a serial communication port. Laos, it is possible to specify tags that enable the programmer to enable/disable reading and writing to the physical device. Specify the following information.

Figure 4.9 Configuration panel ISO-TP4 device definition.

Device Name

Logical name assigned by the user to represent a particular communication device. This field is used as a selection criterion for the next panel: ISO-TP4 Dataset Definition.

| entry | Required |
| --- | --- |
| entry type | Alphanumeric string of up to 16 characters |

TCP/IP address

The Valmet Damatic Computer supports only a serial protocol on the CIS interface, the driver supports the use of an Ethernet-serial switch to connect the serial port through an Ethernet connection. The TCP/IP address of the Ethernet-Serial switch, connecting the FactoryLink station and the Valmet Damatic station, is specified in this field. The field is only used when connecting the Valmet Damatic Computer through Ethernet. The Ethernet address is assumed to be in the format: “192.168.2.1”.

| entry | Optional |
| --- | --- |
| entry type | Alphanumeric string of up to 48 characters |

TCP/IP port

The Valmet Damatic Computer supports only a serial protocol on the CIS interface, the driver supports the use of an Ethernet-serial switch to connect the serial port through an Ethernet connection. The TCP/IP port  used by the Ethernet-Serial switch, connecting the FactoryLink station and the Valmet Damatic station, is specified in this field. The field is only used when connecting the Valmet Damatic Computer through Ethernet.

| entry | Optional |
| --- | --- |
| entry type | Numerical value |

TCP/IP connect

Tag name of a digital tag, the value of this tag determines if the device is connected to or disconnect  from the Ethernet-serial switch. Disabling the connection will stop the communication between the driver and Valmet device. This field is optional and left empty, the TCP/IP connection is enabled. A tag value ON enables the driver to connect to the Ethernet-serial switch, the connection is disabled with a tag value OFF. The field is only used when connecting the Valmet Damatic Computer through Ethernet.

| entry | Optional |
| --- | --- |
| entry type | Tag name, tag type: DIGITAL |

Comm. port

The number of the serial port through which the device must be accessed. Field is required in case the Ethernet address of the Ethernet-serial switch is left empty.

| entry | Optional |
| --- | --- |
| entry type | Alphanumeric string, 1..16. |

Retries

The number of retries that the protocol driver will execute when the Valmet computer does not respond or responds negatively to a request.

| entry | Required |
| --- | --- |
| entry type | Numerial value. |

Timeout

The time out value for the protocol driver, specified in seconds. The protocol driver will wait for the full response to be received from Valmet during the specified number of seconds. If there is no (valid) response within the time out period the driver will retry.

| entry | Required |
| --- | --- |
| entry type | Numerial value. |

Status

Real-time database element written to by the Valmet protocol driver task to indicate the status of a communication command. The status element can be referenced by any task to handle communication error situations. For a detailed list of communication errors see chapter 5.

| entry | Optional |
| --- | --- |
| entry type | Tag name, tag type: ANALOG |

Redefine tables

Real-time database element forced to ON by the user to trigger a rebuild of the set definitions in the Valmet computer. The rebuild is performed in case the database element has the value ON and the change flags are ON. Used in case the Valmet computer has powered on or has lost the definitions downloaded by the driver through some other cause.

| entry | Optional |
| --- | --- |
| entry type | Tag name, tag type: DIGITAL |

Read disable

Real-time digital database element used to enable/disable read commands for the logical device.  Read commands are enabled in case there is no tag defined, or the status of the digital tag is OFF. Read commands are disabled if the status of the tag is ON.

| entry | Optional |
| --- | --- |
| entry type | Tag name, tag type: DIGITAL |

Write disable

Real-time digital database element used to enable/disable write commands for the logical device.  Write commands are enabled in case there is no tag defined, or the status of the digital tag is OFF. Fetch commands are disabled if the status of the tag is ON.

| entry | Optional |
| --- | --- |
| entry type | Tag name, tag type: DIGITAL |

### Valmet Dataset definition

The Valmet Dataset definition panel allows the user to specify datasets for a particular logical device. Different logical device names are selected in the panel Valmet Device definition. Specify the following information.

Select dataset(s) for one device.

Figure 4.10 Configuration panel VALMET dataset definition.

A dataset is a contiguous data area in the device, and is identified with its type, start and length. The IO-Translator mailbox defines the IO-Translator to use for this data set. The maximum number of messages in this mailbox at any given time before the driver stops writing messages into the mailbox is defined with the IO-Translator mailbox.

The dataset tag is a digital tag used to identify the dataset, the same data set tag will be present in the configuration for the IO-Translator. The user is responsible for defining an unique tag name for every data set.

IO-Translator Mailbox Tag

Tag name of a translator mailbox element, to be referenced by the VALMET protocol driver task (N.B. MCI must be supported by the translator task). The I/O translator task uses this mailbox to receive data from the VALMET protocol driver.

| entry | Required |
| --- | --- |
| entry type | Tag name, tag type: MAILBOX |

Name Dataset

Unique name for the data set. The name is used internally in the decoder and protocol driver for activating a data fetch from the external device. A dataset is referenced, internally by the decoder and the protocol driver, by the name. Therefore the name specified in this field must be unique.

| entry | Required |
| --- | --- |
| entry type | Alphanumeric string of up to 18 characters |

Dataset Tag

Tag name representing a (unique) logical name for a dataset. The tag is used internally in the I/O translator and protocol driver for activating a dataset read from the external device. The I/O translator and the protocol driver internally reference a dataset by the tag name defined in this field. As a consequence the tag specified must be unique. The same tag should be used in configuration of the I/o translator to select the conversions for the dataset.

| entry | Required |
| --- | --- |
| entry type | Tag name, tag type: DIGITAL |

Name Set

Unique name for the set that defines the actual contents of this data set. This name is used to link to the set definition panels. The name is used internally in the protocol driver. Therefore the name specified in this field must be unique.

| entry | Required/Optional |
| --- | --- |
| entry type | Alphanumeric string of up to 18 characters |

The name set is optional, actually one does not need to define a name set, if the Dataset name is ‘DEVX’. The dataset name ‘DEVX’ is reserved to retrieve internal data from the driver. In the following table is the dataset defined.

| Element dataset ‘DEVX’ | Description | Type |
| --- | --- | --- |
| Device[20] | Device name. | String (20) |
| TCPIP[20] | TCP/IP address, empty for direct serial connection. | String(20) |
| TCPport | TCP/IP port number, zero for direct serial connection. | Word |
| TCPconnection | Indication if TCP connection is active (1)or disconnected (0), always zero for direct serial connection. | Word |
| COMport | Number of the COMM port for a direct serial connection. | Word |
| Status | Status of the driver | Word |
| Driverenable | Indication of driver enabled (1) or disabled (0) | Word |
| TCPenable | Indication of TCP connection enabled (1) or disabled (0) | Word |
| Disable[2] | Two integers representing the read and write disable of the device; index 0 is read disable and index 1 is the write disable. | Word |
| Count[2] | Two counters representing the number of reads performed (index 0) ands the number of writes performed (index 1) | Long |

The dataset mentioned above is the only dataset that can be written. To write to the dataset ‘DEVX’, no values are needed. Writing to the dataset resets the read and write counters.

## Valmet Set definition

From the display of all the panels, select the Valmet Set definition panel.

Select dataset(s) for one device.

Figure 4.11 Configuration panel VALMET set definition.

The DeltaLink Valmet Set definition panel allows the user to specify the actual contents of a datasets for a particular logical device. Different datasets names are selected in the panel DeltaLink Valmet Dataset definition. The name of the set is device is displayed in the field Table Name, at the bottom of the table. Specify the following information (for details on the meaning the user is also referred to the Valmet Damatic manuals):

Name Set

Text to be filled in by the user for documentation purposes. The text can be used for example to store the corresponding ‘tagname’ within Valmet or to make it easier to define the panels in the decoder (e.g. by inserting here a sequence number). The text is not used by the protocol driver.

| entry | Required |
| --- | --- |
| entry type | Alphanumeric string of up to 20 characters |

Data type

Type definition of the value in the Valmet Damatic computer.

| entry | Required |
| --- | --- |
| entry type | ANALOG refers: A, C, D |
| description | There are 3 types possible: ANALOG (or A or ANA) , COUNTER (or C or COU) , DIGITAL. (or D or DIG). ANALOG specifies an analog 16 bit value for example the level of a tank. COUNTER specifies a 32 bit counter value. DIGITAL specifies to fetch a number of bits (digitals) together with associated status information. The number of bits that is actually fetched depends on the address that is specified. (See further on). |

Bus type

The type of bus to access.

| entry | Required |
| --- | --- |
| entry type | Character: P, C |
| Description | Two bus types are possible: PROCESS (or P) and CONTROL (or C). PROCESS specifies to access the process bus. CONTROL specifies to access the control bus. |

Bus number

Specifies the number of the bus to access.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..7 |

Station number

Specifies the number of the station to access.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..15 |

Block message

Specifies the number of the block to access within the station.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..7 |

Signal group

Specifies the number of the group to access within the block message.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..3 |

Signal

Specifies the signal to access within the group.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..3 |
| Description | In case a COUNTER value is accessed, the signal number should be 0 or 2. |

Signal byte

Specifies (in case of a digital signal only) the byte to access.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..1 |
| Description | For non-digital signals this value must be 0. For digital signals: if 0 is filled the lower byte is accessed., if 1 is specified the higher byte is accessed. |

Data direction

Specifies the data direction.

| entry | Required |
| --- | --- |
| entry type | Numerical value 0..15 |
| Description | In case data from a process station is accessed, a 0 must be specified. Otherwise 1 value greater than 0 must be specified. The number then specifies the control room station to access. |

### Additional remarks

#### Size restrictions

For an external system to be able to access values in the Valmet Damatic computer, the external system must carry out a two-stage action.

- First, the external system must define the values that need to be accessed. The definition must be sent to the Valmet computer;

- Second, data can be read by accessing the definitions that have been previously sent.

The protocol driver takes care of sending the definition for a dataset to Valmet the first time a dataset is accessed after start-up of the driver of the first after a ‘table redefine’ is requested (see the description of the Device panel).

Due to protocol limitations, a dataset can access at most 32 values. Counter values are twice as large and are counted double. So one can define in a dataset at most 32 analog/digital values or at most 16 counter values. If counter values and non-counter values are mixed the number of values in a dataset ranges between 16 and 32.

Due to limitations on the size of the definition table in the Valmet computer, each device can define at most 200 values in all the sets that belong to the device. Counter values are twice as large and are counted double. So one can define in all datasets of a device at most 200 analog/digital values or at most 100 counter values. If counter values and non-counter values are mixed the number of values in a device ranges between 100 and 200.

If the user makes a device and/or dataset definition that violates these constraints, the driver will report the error and exit immediately.

#### Errors in set definitions

In case the user defines an Valmet address in a set that does not exist or defines an address that does not match the defined datatype (for example specifying the datatype DIGITAl in the protocol driver while the value is actaully an analog value) results in Valmet returning 2 bytes (or 4 in case of a counter) filled with the hexadecimal value FF. A corresponding converted (!) value will be displayed by FactoryLink.

#### Translator tag definitions

To access the values read from the Valmet device, the user needs to define Decoder panels accordingly. For the Valmet driver some special precautions must be taken. These precautions will be described below.

Due to the nature of the Valmet Datamatic CIS interface it is not possible to use absolute addressing. Relative addressing must be used.

The address field must be filled as follows:

- fill 0 to access the fault code that Valmet always sends back.

- the address of the entry in the Decoder dataset that matches the entry <n> in the corresponding protocol driver dataset is computed from the address of entry <n-1> by adding 1 to the previous address if entry <n-1> is analog or digital and by adding 2 to the previous address if entry <n-1> is a counter.

Analog values

For analog values the Valmet computer sends, apart from the value itself, also status-like information related to the value. To access ‘status’ information and store it in a digital tag, you must specify the same address as for the analog value itself and use a bit field as follows:

Controller output value

- fill 0 to access the fault code for a controller output value

- fill 1 to access the auto/manual status for a controller output value

Measurement result

- fill 0 to access the O.K. status (value 0) or fault in process connection error (value 1) for a measurement result.

- fill 0 to access the range overflow error (value 1 if overflow).

Digital values

For every digital value defined in the Valmet set, the Valmet computer sends back 8 bits (depending on the signal byte) and, depending on the type of value in Valmet, some status information. To access ‘bit’ and ‘error’ information and store it in a digital tag, you must specify the address as explained above and use a bit field as follows (the titles specify the type of value that is accessed in Valmet):

Information of 4 controlled selector switches

- fill for selector <i> (i=0..3) <8+2*i> to access the open (value 0) or closed (value 1) position of the switch.

- fill for selector <i> (i=0..3) <9+2*i> to access whether the switch is in intermediate position (value 1) or not (value 0).

- fill 0 or 1 to access general error information for this area.

Information of 8 switches

- fill for selector <i> (i=0..7) <8+i> to access the open (value 0) or closed (value 1) position of the switch.

- fill 0 or 1 to access general error information for this area.

Information about controller mode

- fill 0 to access whether the output indicates continous control (value 0) or indicates the need to change control (value 1).

- fill 1 to access whether the controller is on tape 1 (value 0) or on tape 2 (value 1).

- fill 2 to access whether the block operates as a controller (value 0) or as a integrator (value 1).

- fill 3 to access whether a computer set value exists (value 1)or not (value 0)

- fill 4 to access whether a remote set value exists (value 1)or not (value 0)

- fill 5 to access whether Damatic controls the setpoint (value 0) or whether the computer controls the setpoint (value 1).

- fill 6 to access whether the controller is in local mode (value 0) or remote mode (value 1).

- fill 7 to access whether the controller is in manual mode (value 0) or auto mode (value 1).

Conversion types

In the decoder you must also specify a conversion to access the requested (analog) value. Fill the conversion type as follows:

To access the analog value itself, specify ANALOG.

To access the lower alarm limit , specify ANALOG.

To access the upper alarm limit , specify ANALOG.

To access the TI or KN parameter, specify ANALOG.

To access the Kp or TD parameter, specify ANALOG.

This page is left blank intentionally.

# Valmet protocol driver error codes

The error code is returned to the user in a user-defined status tag. These error codes will also be printed with the message of the DeltaLink Valmet protocol driver in the run-time manager. The errors can be generated from different parts of the driver which will be listed here:

| Error # | (Serial) communication errors |
| --- | --- |
| 301 | Open function returned OS error code |
| 302 | Close function returned OS error code |
| 303 | Error retrieving port settings |
| 304 | Error setting port settings |
| 305 | Memory allocation error, rx or tx buffer |
| 306 | Read error serial device |
| 307 | Write error serial device |
| 308 | Read timeout |
| 309 | Error reading time out values for device |
| 310 | Error setting time out values for device |
| 311 | Invalid mode for deivce |
| 312 | Hardware break condition |
| 313 | Framing error |
| 314 | Hardware IO error |
| 315 | Overrun error input buffer |
| 316 | Parity error |
| 317 | Receive buffer overflow |
| 318 | Transmit buffer overflow |
| 319 | Error creating semaphore |
| 320 | Error releasing semaphore |
| 321 | Error closing semaphore |
| 322 | Timeout waiting for lock on device |
| 323 | OS error locking serial device |
| 324 | Error executing break state |
| 325 | no pool of communication ports exist |
| 326 | Error adding com port to pool |
| 327 | no free port could be found |
| 328 | Error setting baudrate |
| 329 | invalid thread id |
| 330 | invalid purging serial buffer |
| 331 | error setting signal mask |
| 332 | wrong number of data bits |
| 333 | wrong number of stop bits |
| 340 | modem command error |
| 341 | Calling winsock stack failed |
| 342 | Invalid winsock version found |
| 343 | Creation of socket failed |
| 344 | Connection to remote host failed |
| 345 | Error sending TCP data |
| 346 | Error receiving TCP data |
| 347 | Connection needed, but no present on connection |

| Error # | VALMET driver status / errors |
| --- | --- |
| 350 | Read functionality has been disabled by the user |
| 351 | Write functionality has been disabled by the user |
| 352 | The com port could not be opened. |
| 353 | An incorrect BCC was returned by Valmet device. |
| 354 | An invalid type of answer was returned by Valmet device. |
| 355 | An invalid data length was returned by Valmet device. |
| 356 | An invalid number of words was returned by Valmet device. |
| 357 | A time out occurred before a valid or expected message was returned. |
| 358 | Extraneous characters followed the checksum byte. |
| 359 | The message returned by Valmet had an unexpected composition. |
| 360 | A read/write was requested while thedriver was disabled with the disable-tag. |
| 361 | A read/write was requested, using the TCP layer, with the TCP-connection disabled. |
| 362 | The maximum number of words for the specified dataset is exceeded, reconfigure the dataset and shorten it. |
| 363 | Timeout receving an ‘ACK’ from the Valmet device, read/write request is aborted. |
| 364 | Unsupported read or write request, request ignored. |
| 365 | Internal error |

| Error # | FactoryLink errors |
| --- | --- |
| 401 | Internal error, general error code |
| 402 | Out of memory, memory allocation error because of a system exhaustion or FactoryLink allocation |
| 403 | Unable to map kernel semaphores |
| 404 | Can not locate real-time database for given {FLNAME} |
| 405 | Can not locate real-time database for given {FLDOMAIN} + {FLUSER} |
| 406 | Incorrect function, reserved error code |
| 407 | Incorrect argument, bad input parameter passed into function |
| 408 | TAG structure received with an invalid offset member |
| 409 | TAG structure received with an invalid type or offset member |
| 410 | Null pointer assignment |
| 411 | Change read/wait function call failed because no changes for given tag array |
| 412 | Procedure table full, maximum number of tasks has registered for the given {FLNAME}/{FLDOMAIN}/{FLUSER} |
| 413 | Bad procedure name |
| 414 | Bad user name |
| 415 | Bad option |
| 416 | Incorrect checksum |
| 417 | No options |
| 418 | No key |
| 419 | Bad key |
| 420 | No port available |
| 421 | Port busy |
| 422 | Initializing task with same name as one currently running |
| 423 | Attempted to unlock the kernel, without holding a lock |
| 424 | Unable to attain lock to the kernel |
| 425 | Attempted to release a lock that has expired on the kernel |
| 426 | Invalid task ID passed into fl_wait() |
| 427 | Termination flag for given task ID set to ON |
| 428 | Internal error, failed to allocate mailbox queue |
| 429 | Internal error, inconsistent queue size |
| 430 | Reserve, no tag list |
| 431 | Reserved, tag list changed |
| 432 | Failure occurred awakening task sleeping on the kernel |
| 433 | No signals pending for caller |
| 434 | Task awakened by signal from another task |
| 435 | Called mailbox function with a tag not f type MAILBOX |
| 436 | No mailbox message pending for mailbox tag |
| 437 | Can not read a mailbox message targeted for another task |
| 438 | Attribute name table full |
| 439 | Invalid attribute name |
| 440 | Cannot find requested attribute |
| 441 | Attempted to start application with same {FLNAME} as one running |
| 442 | Unable to map to kernel memory area for {FLNAME} |
| 443 | Task protection bit not set for initializing task |
| 444 | Attempted to start restricted task from running on a lite system |
| 445 | Unable to get or release semaphore |
| 446 | Mailbox message space exhausted |
| 450 | Float (FLP) is not-a-number |
| 451 | Float (FLP) is positive infinity |
| 452 | Float (FLP) is negative infinity |
| 501 | FLDTP general failure indicator |
| 502 | FLDTP invalid argument passed dtp function |
| 503 | FLDTP invalid tag passed to dtp function |
| 504 | FLDTP memory allocation failure |
| 505 | FLDTP can not find requested object |
| 506 | FLDTP illegal call to procedure at given time. Some dtp functions are not re-entrant |
| 507 | FLDTP kernel function call failed. |
| 508 | FLDTP tag of unknown type passed into function |
| 509 | FLDTP no tag changes are pending |

| Error # | MCI errors |
| --- | --- |
| 550 | Bad message type |
| 551 | Message with dataset control tag not found in queue |
| 552 | No messages available to query |
| 553 | Bad receive mailbox tag |
| 554 | Bad mailbox send tag |
| 555 | Bad dataset control tag |
| 556 | Message cannot be adjusted |
| 557 | Operation to big for variable |
| 558 | Unknown boundary |
| 559 | Function not supported |
| 560 | No message for this index present |
| 561 | The remote dataset Is not defined on this system |
| 562 | The received dataset was not registered |
| 563 | The message is not queued |
| 564 | Message is rejected due error in the remote MCI |
| 565 | Illegal method of addressing bits on bit boundary |
| 566 | Element cannot be written |
| 567 | Invalid buffer specified |
| 568 | Block write function impossible |
| 569 | Maximum number of messages in MBX reached |
| 570 | No memory left |
| 571 | Error registering standard dataset |
| 572 | Error writing message in pipe |
| 573 | Not supported MCI message |
| 574 | Error creating pipe |
| 575 | Error starting threat |
| 576 | Error server connecting to pipe |
| 577 | Error child connecting to pipe |
| 578 | Error reading the pipe |
| 579 | Error number of bytes read from pipe |
| 580 | Error writing into the pipe |
| 581 | Error number of bytes written into the pipe |
| 582 | Error reading dataset from the mailbox |
| 583 | No communication buffers assigned |
| 584 | Error decrementing semaphore |
| 585 | Error writing to pipe, no space left |
| 586 | Error querying no. of messages for translator |
| 587 | Max. No. of messages in translator MBX reached |

This page is left blank intentionally.

# Valmet protocol driver  error messages

If an error condition occurs in the protocol driver task during run-time mode, a message to that effect will appear on the runtime manager graphics screen to the right of "Valmet". The error messages that may be displayed are as follows:

Can't open CT file

The protocol driver task was unable to open the configuration table file, generally because it does not exist. This is a fatal error.

No triggers defined

The protocol driver configuration table file does not contain an expected trigger. This is a fatal error.

No Datasets defined

The protocol driver configuration table file does not contain a valid dataset definition. This is a fatal error.

No Decoders defined

The protocol driver configuration table file does not contain a valid decoder definition. This is a fatal error.

Unknown decoder table %s record %d type %d

The protocol driver configuration table file contains an unknown decoder mailbox tag, for the specified table, record number and type of dataset. This is a fatal error.

Reading CT index

An error occurred during reading a Configuration Table index, normally this means the CT-file is corrupted. This is a fatal error.

Reading CT header

An error occurred during reading a Configuration Table header, normally this means the CT-file is corrupted. This is a fatal error.

Reading CT record

An error occurred during reading a Configuration Table record, normally this means the CT-file is corrupted. This is a fatal error.

Out of RAM

There is not enough RAM memory to load the complete configuration and/or task.

Invalid tag number

The protocol driver encountered an invalid TAG number. This is a fatal error.

Bad tag %s %s %d

The protocol driver encountered an incorrect TAG definition. The device, functionality  and the error number are displayed.

Reading data %s %s, %d

The protocol driver encountered an error reading a TAG. The device, functionality  and the error number are displayed.

Mbx query %s mbx, %d

The protocol driver encountered an error reading a mailbox TAG. The name of the TAG and the error number are displayed.

Change read %s %s, %d

The protocol driver encountered an error during a change read of a TAG. The device, functionality  and the error number are displayed.

Forced write %s, %d

The protocol driver encountered an error during forced writing a TAG. The device and the error number are displayed.

MCI init %d

MCI initialisation error, internal error of the protocol driver task. Specified is the error number.

MCI maximum msg in Decoder MBX %d reached

MCI error, the maximum number of allowed messages in a decoder mailbox tag is reached. Specified is the record number of the decoder mailbox.

MCI initialising PD queue %d

MCI initialisation error, internal error of the protocol driver task. Specified is the error number.

MCI receive from PD mailbox %d

MCI error, internal error of the protocol driver task. Specified is the error number.

MCI write to send mailbox %d

MCI error, internal error of the protocol driver task. Specified is the error number.

MCI search control tag %d,%d device %s %d

MCI error, internal error of the protocol driver task, a previously registrated command in the mailbox could not be found. Specified are the dataset control tag, device name and the error number.

MCI get number of messages %s

MCI error, an error occurred during reading a mailbox tag element. Specified is the error number.

MCI identify dataset by number not supported %d

MCI error, decoder tried to identify a dataset by a number. This is not supported in this version of the protocol driver. Specified is the dataset number.

MCI received msg couldn't be converted to dataset

MCI error, a received message in the mailbox tag element is not recognised as a valid read or write command.

MCI msg adjust %s on ds %d:%d: %d

MCI error, a received message in the mailbox tag element could not be interpreted as a valid read or write command for the external device. Specified are the device name, dataset control tag and the error number.

MCI unknown msg type %d

MCI error, internal error of the protocol driver task. Specified is the number of an unrecognised command.

MCI Bad MSG Control TAG table %s record %d type %d

MCI error, internal error of the protocol driver task. Specified are table number, record number and type number.

MCI Duplicate MSG Ctrl TAG table %s record %d type %d

MCI error, internal error of the protocol driver task. Specified are table number, record number and type number.

MCI Bad Mailbox TAG table %s record %d type %d

MCI error, internal error of the protocol driver task. Specified are table number, record number and type number.

MCI DS for %s function not found, MsgCtrl %d

MCI error, internal error of the protocol driver task, missing dataset for the task. Specified are function and the message control TAG.

Com init comm layer %d

An error occurred during initialising the communication layer Specified is the error number.

Device %s. Error while communicating %s

Status message for the specified device and function. The meaning of the error number can be found in the previous appendix.

Com building device

An error occurred during building the communication datablock for device. This is a fatal error.

Internal error

Internal error of the protocol driver task, contact DeltaLink Benelux for support.

Too many entries in set %s. Number is %d.

The set with the given name violated the size restrictions for a set. The number of entries in the set is given (where counters count double.)

Too many entries in device %s. Number is %d.

The device with the given name violated the size restrictions for a device. The number of entries in the device is given (where counters count double.)

Internal error

Internal error of the protocol driver task, contact DeltaLink Benelux for support.