

 
[image: image32.png]


   

[image: image33.png]



 




[image: image38.png]1S0 TP4/CLNP Configuration

Local Address [TECHNICS T

NSAP [TECHNICST6

oK Cancel He




DeltaLink SINEC_H1

[image: image2.wmf]
DeltaLink SINEC_H1

Sinec H1 Bus interface software for FactoryLink

User Manual


Table of Contents

41. 
Introduction

1.1. 
Scope of this document
4
2. 
Contents of shipment
6
3. 
Installation
8
3.1. 
Installation of the FactoryLink software
8
3.2. 
Installation of the Ethernet Stack
10
3.3. 
Installation of the protection
11
3.3.1. 
The DeltaLink option file
11
3.3.2. 
Demo installation
11
4. 
Principle
13
4.1. 
The decoder RAP Ddriver principle
13
4.2. 
H1 Communication
14
4.2.1. 
Datasets
14
4.2.2. 
Virtual connection
16
4.2.3. 
Block read and block write
17
4.2.4. 
Exception write
17
4.2.5. 
Encoded write
17
4.2.6. 
Unsolicited receive
19
4.3. 
FactoryLink domain selection
20
5. 
Configuration tables
22
5.1. 
Mailbox definition
23
5.2. 
Decoder definition
24
5.3. 
Device definition
25
5.4. 
Dataset definition
29
Appendix A. Communication OSI protocol stack installation
35
A.1 OSI protocol stack for Windows NTI
35
Appendix B. Command line parameters
38
Appendix C. Sinec H1 protocol driver error codes
39
Appendix D. Messages
43
Appendix E. Siemens S5-PLC
46
E.1 Encoded write handling
46
E.2 Unsolicited receive PRIO 4
48
E.3 CP143/CP535 Configuration
50
E.4 PLC Software example
52
Appendix F. Siemens S7-PLC
54
F.1 S7 H1 protocol
54
F.2 Encoded write handling
58
F.3 CP443 Configuration
60
F.4 PLC Software example
65



This page is left blank intentionally.


Introduction

Thank you for buying this driver! We hope you will enjoy using this product.


Scope of this document

This manual is written for a technician who is familiar with both the FactoryLink® IV software and the Siemens S5 or Siemens TI Programmable Logic Controllers (PLC's). This document can be used both as a training manual as well as a reference manual.

Note: Please check the contents of the shipment with the list as described in the next chapter.

The first section of this manual deals with the installation of hardware and software in your FactoryLink workstation. This part is split into a platform independent and a platform specific part. Please read carefully through both parts to make sure both hardware and software are installed correctly.

The second part explains the operation principles of the communication with the Siemens PLC and the Decoder. Here all terms and definitions are explained to the reader. It ex​plains terms like "Dataset" and "Virtual Connections'. This part should be read by both the PLC programmer and the FactoryLink programmer to make sure that the optimum per​for​man​ce can be achieved.

The third part explains the exact tables associated with this driver. This part is useful only to FactoryLink programmers and can be used as a reference. This part is also an example of how to use this driver with the Decoder. It shows the entries made for the pre-configu​red demo which comes with this package. The demo pro​gram can be used to check if the com​munication is working without making a complete application.

The last part are the appendices which contain summarised data.

®Copyright1997 by DeltaLink bv, The Netherlands. All rights reserved.

DeltaLink is a registered trademark, The Netherlands.

FactoryLink is a registered trademark of United States Data Corporation, Richardson Texas USA.

DeltaLink bv, Pioenroosstraat 26, 5241AB Rosmalen, The Netherlands, 

tel + 31 73 523 1234

fax +31 73 523 1222

This page is left blank intentionally.


Contents of shipment


Please check the package you received with the checklist below. Should there be an item missing contact DeltaLink bv to correct the problem. There is a limit of 90 days after shipment to report problems!

This package includes the following:

(
A Sinec H1 driver build contained on the FactoryLink Device Inteface CDROM media or on a diskette(s) labelled "DeltaLink Sinec H1 Protocol Driver" 


This manual.

You should also have:


A IMX based decoder e.g. DeltaLink decoder.

The correct hardware and software for the OSI Ethernet stack on your platform. (See also chapter 3)


Siemens or TI PLC with H1 communication board and software to program both the CPU and the CP boards.


An Ethernet-network with at least both the PLC and the FactoryLink station connected to it.

This page is left blank intentionally.


Installation


Installation of the FactoryLink software

To install the FactoryLink task and its related tables please follow the following steps.

Before installing

Before installing the driver on the system, FactoryLink must have been installed error free. It is very important that all the environment settings are made for the FactoryLink system such as the FLINK, FLOPT etc.

First:

Copy the files from the "DeltaLink SINEC_H1" media to the appropriate directory. This will be done automatically by running the install utility placed on the installation media. The installation procedure differs for UNIX and W95-OS/2-NT systems.

For W95-OS/2-NT systems follow the next procedure:

a:\SYMBOL 195 \f "Wingdings"
installSYMBOL 195 \f "Wingdings"
For UNIX systems first an install directory must be created. The files on the install media must be first copied to the install directory using the tar command. From this directory the install utility can be run. 

For UNIX systems follow the next procedure:

mkdir install

cd install

tar xv
install
Second:

After you installed the software you need to activate the tables in the FactoryLink Con​fi​gu​ra​tion Manager (FLCM). The installation automatically appends the sinec_h1.ac entry into the {FLINK}/ac/titles file
. The place of this entry is also the place where the option appears in the FLCM Main Menu. Therefore check the validity of the entry and move it to the place where you want to appear it in the Configuration Manager. The entry must match the sinec_h1 entry in the following table:

file: {FLINK}/ac/titles:

...

windhdr.ac

decoder.ac

sinec_h1.ac

spool.ac

...

Third:

To make sure all the Configuration Tables (CT's) are generated after a change, the install utility automatically adds the sinec_h1 entry at the end of the {FLINK}/ctgen/ctlist file. The place of this entry is not important. Check if this entry has the same format as in the next table.

file: {FLINK}/ctgen/ctlist:

...

recipe: rcphdr rcpovr

decoder: decoderm decoderp decoderd decodert

sinec_h1: sinech1m sinech1x sinech1p sinech1d

iml: imltags imltrig

...

Fourth:

To enable the help functionality for the Siemes Sinec H1 Protocol Driver tables in the Configuration Manager, the installation utility reindexes the ‘help-index’ for the Configuration Manager. If desired reindexing of the ‘help-index’ can be started from the command line prompt.

mkhelpSYMBOL 195 \f "Wingdings"
Fifth:
The FactoryLink Configuration Manager uses a map file, {FLINK}/ac/ac2ct.map, to be aware of the different confi​gu​ra​tion tables which can be located behind one entry in the main menu. Upon startup, the Configuration Manager reads the map file instead of all the table configuration files, mainly because reading all these files at once takes too much time. An account manger is present to update this conversion file, and can be started from the command line.

acctmgr  -c -d -t{FLINK}/ac/titlesSYMBOL 195 \f "Wingdings"
Sixth:
The protocol driver must, with the FactoryLink Configuration Manager (FLCM),  be entered in the System Configuration table. An entry of an existing task which will not be used at run-time can be overwritten or a new entry can be created with (as a minimum) the following data:

Task Name
Description   ....   



Executable File

SINEC_H1
Siemens Sinec H1 Protocol Driver

bin/sinec_h1

The Task Name and name of the executable file are fixed and should not be altered by the user.

This completes the installation of the FactoryLink (software) parts.


Installation of the Ethernet Stack

It is necessary to have an Ethernet stack loaded which can be used by the driver to com​mu​ni​cate with the Sinec H1 network. This stack is based on an OSI transport layer 4 protocol. Depending on the platform the stack can be different. Please choose the correct platform and options and make sure your stack is loaded correctly.

A platform dependent description of how to set-up an Ethernet stack for the Sinec H1 network can be found in Appendix A.


Installation of the protection

The Siemens Sinec H1 protocol driver is protected via the DeltaLink option file. This file contains authorization sequence codes for DeltaLink modules. The protection is linked to the serial number of the FactoryLink package.

AUTONUMLGL
The DeltaLink option file

The installation media of the Sinec H1 driver contains an option file, named ‘delta.opt’, in the 'opt' direc​to​ry. This file contains the unique autho​ri​za​tion sequence which enables the Sinec H1 driver to run. The install utility automatically copies the authorization sequence into the {FLOPT}/delta.opt file. It is also possible to enter the authorization sequence manually into the {FLOPT}/delta.opt file. For more information on the delta.opt file refer to Appendix B. 

Note that the task will only run on the FactoryLink system with the same serial number. The delta.opt file on the installation diskette contains, for reference, the serial number of FactoryLink.

AUTONUMLGL
Demo installation

It is possible to install the Sinec H1 driver without an authorization code. This will be done from a normal installation media. In this case the task will start up but only runs in so called 'demo' mode. This means that the driver runs only for a limited period of time (five hours). After this period has expired the task will shutdown and can not be restarted before the complete FactoryLink system has been restarted. 

After  installation of this demo version an authorization code can be ordered and installed which enables the task to run without the time and restart limitation. The authorization code must be entered manually in the {FLOPT}/delta.opt file. For more information on entering the authorization code in the delta.opt file refer to Appendix B. 

The limitations of a demo version of the Siemens Sinec H1 driver are:

- five hours of consecutive run-time

- not restartable (FactoryLink must be restarted)

This page is left blank intentionally.


Principle

AUTONUMLGL
The decoder RAP Ddriver principle

RAPD stands for Rapid Application Protocol Driver. The RAPD principle was adopted so that protocol drivers can be easily and rapidly configured for a FactoryLink application. RAPD is based on the Intertask Mail Exchange Standard or IMX, which defines a way for a protocol driver task to com​mu​ni​ca​te with an I/O Translator task (e.g. Decoder, high speed logger). The RAPD system consists of a protocol driver which communicates with external devices (RTUS, PLCs, etc.) and a translator which controls data storage (going to and coming from a protocol driver) in the FactoryLink real-time database. All data collected by the protocol driver is referenced as contiguous blocks or ranges within the device. This enables communications between the driver and a device to be very efficient. All data is referenced between the driver and the translator in terms of datasets. Datasets, described in the next section, define memory regions or locations of data within a device.

The protocol driver and the IOX communicate with one another via FactoryLink mailbox tags, according to the IMX standard. Every task (translator and protocol drivers) has its own mailbox, so for full communication between a translator and a protocol driver a mailbox database element for every task has to be defined. The IMX standard is especially designed for the following situation. To use one decoder and several protocol drivers. For example the decoder together with the Sinec H1 protocol driver and the Modbus Plus protocol driver. Aside from storage duties, the translator provides data conversions (i.e. analog, IEEE conversions, etc.) for I/O data to/from a protocol driver.




Figure 4.1.1 The RAPD principle.

AUTONUMLGL
H1 Communication

AUTONUMLGL
Datasets

A dataset is a (contiguous) area of data in the PLC. The complete area can be read or written to, with one command (trigger). Except actions on the complete area, the protocol driver is also capable of addressing specific elements (or a group of elements) in the data area. The decoder takes care of mapping the PLC-data to/from FactoryLink Tags (including con​ver​sions). 

A dataset consist out basic elements, which are all of the same size, for example all words or all bytes. This size corresponds with the size definition of the data area in the PLC and is called the boundary of a dataset. The boundaries for the different data areas used with the Sinec H1 driver are listed in the tables below.

Siemens  S5


PLC data type
Boundary

Data block
Word

Flags
Byte

Input
Byte

Output
Byte

Counter
Word

Timer
Word

System word
Word

Peripheral byte
Byte

Extended Peripheral byte
Byte

Expanded data block
Word

Siemens  S7


PLC data type
Boundary

Data block
Byte

Flags
Byte

Input
Byte

Output
Byte

Siemens  TI


PLC data type
Boundary

Data block
Byte

Flags
Byte

Input
Byte

Output
Byte

Variable
Word

Constant
Word

Discrete Input
Byte

Discrete Output
Byte

Control Register
Byte

Discrete Input Packed
Byte

Discrete Output Packed 
Byte

Control Register Packed
Byte

Word Input 
Word

Word Output 
Word

Timer or Counter Preset 
Word

Timer or Counter Current
Word

Drum Step Preset 
Word

Drum Step Current
Word

Drum Counter Preset 
Word

System Status words
Word

Drum Current count
Long

Variable Memory
Word

Constant Memory
Word

Loop Status
Word

Loop Mode
Word

Loop Gain
Long

Loop Reset time
Long

Loop Rate time
Long

Loop High Alarm Limit
Long

Loop Low Alarm Limit
Long

Loop Process Variable
Long

Loop High Process Var.
Long

Loop Low Process Var.
Long

Loop Orange Deviation
Long

Loop Yellow Deviation
Long

Loop Sample Rate 
Long

Loop Set Point
Long

Loop Output
Long

Loop V-flags
Long

Loop Control Flags
Word

Loop Ramp/Soak Status
Word

Loop Error
Long

Loop Bias
Long

Loop Process Variable High High Alarm
Long

Loop Process Variable Low Low Alarm
Long

Loop Rate Change Alarm
Long

Loop Setpoint High Limit
Long

Loop Setpoint Low Limit
Long

Loop Alarm Deadband
Word

Loop Raw High Alarm Limit
Word

Loop Raw Low Alarm Limit
Word

Loop Raw Process Variable
Word

Loop Raw Orange Dev Alarm Limit
Word

Loop Raw Yellow Dev Alarm Limit
Word

Loop Raw output
Word

Loop Raw setpoint
Word

Loop Raw Error
Word

Loop Raw High/High Alarm Limit
Word

Loop Raw Low/Low Alarm Limit
Word

Loop Raw Alarm Deadband
Word

Loop Raw Bias
Word

Loop Raw Setpoint Low Limit
Word

Loop Raw Setpoint High Limit
Word

Loop Most-sig word loop C-flags
Word

Loop Least-sig word loop C-flags 
Word

Loop Derative Gain Limiting Coef
Long

Loop Ramp Soak Step Number
Word

Loop Alarm Acknowledge Flags
Word

High Alarm Limit
Long

Alarm Limit
Long

Process Variable
Long

Process Variable High Limit
Long

Process Variable Low Limit
Long

Orange Deviation Alarm Limit
Long

Yellow Deviation Alarm Limit
Long

Sample Rate in seconds
Long

Alarm Setpoint
Long

Alarm Variable Flags
Word

Alarm Control Flag
Word

Alarm Error
Word

High High Alarm Limit
Word

Low Low Alarm Limit
Word

Rate of Change Alarm Limit
Word

Setpoint High Limit
Word

Setpoint Low Limit
Word

Alarm Deadband
Word

Raw High Alarm Limit
Word

Raw Low Alarm Limit
Word

Raw Process Variable
Word

Raw Orange Deviation Alarm Limit
Word

Raw Yellow Deviation Alarm Limit
Word

Alarm Raw Setpoint
Word

Raw Alarm Deadband
Word

Alarm Raw Error
Word

Raw High-High Alarm Limit
Word

Raw Low-Low Alarm Limit
Word

Raw Setpoint Low Limit
Word

Raw Setpoint High Limit
Word

Most-sig word Alarm C-flags
Word

Least-sig word Alarm C-flags
Word

Alarm Acknowledge Flags
Word

VME (TI575 only) A24 space
Word

VME (TI575 only) 16 space
Word

App Z global variables
Word

App Y global variables
Word

App X global variables
Word

App W global variables
Word

App V global variables
Word

App U global variables
Word

App T global variables
Word

App S global variables
Word

App R global variables
Word

App Q global variables
Word

App P global variables
Word

App O global variables
Word

App N global variables
Word

App M global variables
Word

App L global variables
Word

App K global variables
Word

App J global variables
Word

App I global variables
Word

App H global variables
Word

App G global variables
Word

App F global variables
Word

App E global variables
Word

App D global variables
Word

App C global variables
Word

App B global variables
Word

App A global variables
Word

Local App global variables
Word


Virtual connection

Data exchange between a FactoryLink workstation and a PLC is performed by using the read- and write-services of e.g. the Siemens CP535/CP143 communication processor. The pro​tocol driver task uses the read-service to read (or fetch) data from the PLC, and it uses the write-service to write data to the PLC. Both actions can be initiated by the driver task, also the PLC may use the write-service for sending data to the FactoryLink station, the unsolicited receive for the protocol driver.

Every read/write/receive-service is associated with a so called Virtual Circuit (VC). A Virtual Circuit is a bi-directional point-to-point communication link through the network. Each Virtual Circuit re​quires a Transport Service Access Point Identifier (TSAP-ID). To set-up a Virtual Connection between two stations, the following information is needed for each station.


-
Local Ethernet address.


-
Local TSAP.


-
Remote Ethernet address.


-
Remote TSAP.

The Sinec H1 protocol supports different types of read and write services, the ones supported are described in the next paragraphs. In the table below are all the possible services listed together with the information if they are supported or not.

Read/Write Service
Supported

Block read
Yes

Block write
Yes

Exception write
Yes

Encoded write
Yes

Unsolicited Receive
Yes


Block read and block write

The block read and block write commands are performed on a contiguous block of data in the PLC,  the dataset. Both commands are initiated by the FactoryLink station. The decoder sends re​quests to the Sinec H1 protocol driver for reading or writing an entire dataset. For configu​ring the decoder refer to the manual of the decoder.


Exception write

An exception write is initiated by the FactoryLink workstation, and writes data to the PLC. Not a complete dataset but one element from the dataset is written to the PLC. The protocol driver will receive a request for an exception write from the decoder. The first action the driver will take is to check if the write can be accomplished with one write or must be read first.

In case the exception data element size is smaller than the size of the PLC data type element (boundary) the data must be read first, patched with exception data and written back. If this is not done, data will be unintentionally overwritten in the PLC. Whether this is the case depends on the data type of the dataset.

For example a Siemens S5 PLC: if a data left (DL) in a Data Block (DB) has to be set then the specific data word has to be read first because the smallest element in a Data Block is a word. The DL has to be patched into the word and written back.

In the above mentioned example it is possible, that the device changes the contents of the word, after the protocol driver has read the word, but before the new value is written. This means that after the write of the protocol driver the content change of the PLC is lost. For  applications which require that single elements can be accessed both by the PLC and the protocol driver, an encoded write can be used. The encoded write will be discussed in the next section.


Encoded write

The encoded write function is almost similar to the exception write in the fact that both functions write single data elements. The difference is that the exception write accesses directly the destination address in the PLC, whereas the encoded write composes an encoded write command and writes this command to a location in a certain data block. The PLC program reads and decodes this encoded write command and accesses the actual destination location.

The advantage of this method is that for every element to write only one write command is needed because the PLC program does the actual operation on the data element (no reading before writing). Another advantage is that the PLC program can control all encoded writes because they all are written to one location in the PLC. For a complete description and the lay-out  of an encoded write command refer to Appendix E and Appendix F .

The location where the encoded write command will be placed is part of the definition of a logical device, a detailed description is in the next chapter.


Unsolicited receive

In case of an unsolicited receive the PLC sends a dataset to the FactoryLink workstation, without a specific request from that workstation. This means that the action is initiated by the PLC. The protocol driver will check if the received data is configured in one of the datasets. If this is the case, the data will be sent with the dataset information to the decoder which con​verts and updates the data. If no dataset is specified regarding to the received data, it will be discarded.

The unsolicited receive function is a very powerful functionality for fast communication be​cau​se no request has to be placed by the protocol driver. This way less overhead is invol​ved in communication. Data which alters unpredictably such as alarms are very suitable for the unsolicited receive function. Some extra programming effort has to be done in the PLC becau​se the PLC is in charge of sending the data.

AUTONUMLGL
FactoryLink domain selection

The standard domain for the Siemens Sinec H1 protocol driver is the SHARED domain. The protocol driver communicates with a dedicated piece of hardware, there fore only one task should be able to access the hardware. If only one program accesses the hardware, the task should be located in the shared domain and therefore started by the shared runtime-manager.

Important: The protocol driver and the decoder must be in the same domain (either SHARED or USER).




Figure 4.3.1 Standard domain selection.

This page is left blank intentionally.


Configuration tables

In the Configuration Manager Main Menu, select DeltaLink Sinec H1 Protocol Driver. Four tables appear, with the titles of all panels visible for direct access. To access a specific panel position the cursor on a visible area and press the left mouse-button, or use the Next/Prev but​tons .

Note: For general information about entering data in FactoryLink configuration tables, refer to the FactoryLink Fundamentals Manual.

[image: image3.png]DeltaLink H1 Mailbox defi

Edt View Uilties Est Help

(O[]

Protocol Driver Local Tsap E
Mailbox Tag
SINEC_HIMBX 5 | FLINK

L
Cancel Enter Exit Next Prev





[image: image4.png]Edt View Uilties Est Help

(O[]

Decoder Max MSG Description E
Mailbox Tag
DECODERMBX 5 | 100 Decoder Mailbox =

Cancel

Enter

Next

Prev.





[image: image1.wmf]RAPD

[image: image32.png][image: image5.png](O[]

Edt View Uilties Est Help

Device Name Devicr | Ethemethddress | RemoteRead | Read | Remowwie |~
Type Tap Prio Tsap
PLCT 57 80006010001 FETCH z RECEVE
L
Cancel Enter | Next Prev





[image: image33.png][image: image6.png](O[]
Edi View Uiites Bt Hop
Decoder Data Set Tpe [ 08 [ Sen | tengn ] -
Mailbox Tag
DECODERMBX S | DataSet(0] 0B 50 z 70
DECODERMBX S | DataSet[1] 0B 50 3 2
DECODERMBX S | DataSet[2] 0B 50 10 14
DECODERMBX S | DataSet(3] 0B 50 10 14
DECODERMBX S | DataSet(d] 0B 50 10 14
DECODERMBX S | DataSet[s] 0B 10 0 . [
DECODERMBX S | DataSet[6] 0B 50 30 36
DECODERMBX_S | DataSet(7] 0B 50 30 36
e e m—
Cancel | Enter || B | Next Prev |





Figure 5.0.1 Siemens Sinec H1 Configuration panels.

AUTONUMLGL
Mailbox definition

From the display of all the panels, select the DeltaLink H1 Mailbox Definition panel.

[image: image7.png]DeltaLink H1 Mailbox defi

Edt View Uilties Est Help

(O[]

Protocol Driver Local Tsap E
Mailbox Tag
SINEC_HIMBX 5 | FLINK

L
Cancel Enter Exit Next Prev





Figure 5.1.1 DeltaLink H1 Mailbox Definition.

The Siemens H1 mailbox definition panel allows the user to initialise one Mailbox Tag for the Sinec H1 pro​to​col driver. Only one Mailbox is needed for full performance of IMX. Specify the following information.



Protocol Driver Mailbox Tag

Tag name of the Sinec H1 protocol mailbox element that the developer defines, to be refe​ren​ced by a decoder task (N.B. IMX must be supported by the decoder task). The decoder task uses this mailbox to send requests to the Sinec H1 protocol driver.

entry: 

Required.

entry type: 
Standard FactoryLink tag name.

valid entry: 
MAILBOX.



Local Tsap
Local  TSAP identifier of the FactoryLink workstation. The entry made here must be iden​tical with the remote TSAP identifier of the connected device(s).

entry: 

Required.

entry type: 
Alphanumeric string.

valid type: 
String of up to 8 characters.



Description
Description of the Sinec H1 protocol driver mailbox element defined by the developer.

valid entry: 
Output only.


Decoder definition

From the display of all the panels, select the DeltaLink H1 Decoder definition panel.

[image: image8.png]Edt View Uilties Est Help

(O[]

Decoder Max MSG Description E
Mailbox Tag
DECODERMBX 5 | 100 Decoder Mailbox =

Cancel

Enter

Next

Prev.





Figure 5.2.1 DeltaLink H1 Decoder Definition.
The  Sinec H1 Decoder Definition panel allows the user to specify one or more decoder(s). Every decoder mailbox tag specifies a different decoder. Only one mailbox tag, for every decoder, is needed for full performance of IMX. Specify the following information.



Decoder Mailbox Tag

Tag name of a decoder mailbox element, to be refe​ren​ced by the Sinec H1 protocol driver task (N.B. IMX must be supported by the decoder task). The decoder task uses this mailbox to receive data from the Sinec H1 protocol driver.

entry: 

Required.

entry type: 
Standard FactoryLink tag name.

valid entry: 
MAILBOX.



Max MSG

The maximum number of requests for the protocol driver, which can be queued in the mailbox tag. Recommended is a value of 100 messages. The number of messages is limited by the size of an integer value (9999), and practically by the amount of available memory. The memory needed for a request depends on the size of the configured datasets.

entry: 

Required / Default: 100.

entry type: 
Decimal number.

valid entry: 
Positive integer 1 .. 9999.



Description
Description of the decoder mailbox element defined by the developer.

valid entry: 
Output only.


Device definition

From the display of all the panels, select the DeltaLink H1 Device Definition panel.

[image: image34.wmf]
Figure 5.3.1 DeltaLink H1 Device Definition.
The DeltaLink  H1 Device definition panel allows the user to specify logical devices, for the communication. Different logical device names may be used for one communication de​vice (the same Ethernet address). If the same Ethernet address is used make sure that the next entries are not identical: Device Name, Remote TSAPs. Specify the following infor​ma​tion.



Device Name
Logical name assigned by the user to represent a particular communication device. This field is used as a selection criterion for the next panel: DeltaLink H1 Dataset Definition
entry: 

Required.

entry type: 
Alphanumeric string.

valid type: 
String of up to 16 characters.



Device Type
PLC type of the logical device. This type specifies wich dataset types are present in the PLC.

entry: 

Required.

entry type: 
Alphanumeric string.

valid entries: 
S5, S7, S7RW, SYM, TI.


description: 

PLC type
Description

S5
Siemens S5 PLC, standard H1

S7
Siemens S7 PLC, with handling blocks, read/write information is supported

S7RW
Siemens S7 PLC, without handling blocks, no read/write information

SYM
Symadyn controller, no read/write information

TI
Siemens Texas Instruments PLC



Ethernet address

The PLC Ethernet address. A six byte (00 - FF) address to identify the PLC in the Ethernet network for example 080006010001. This address must be specified in case the H1-TP4 protocol is used for communication with the PLC. This field can be left blank in case the H1-TCP protocol is used and the next field has to be specified. It is also possible to change the MAC address dynamically in case a tag has been specified. When defining a tag then a default value as a MAC address must be specified.

entry: 

Optional.

entry type: 
Hexadecimal string or TAG.

valid entry:
String of up to 12 characters.



TCP/IP address

The PLC TCP/IP address. This must address according to the syntax of the Internet Protocol i.e. 192.0.0.0. This address must be specified in case the H1-TCP protocol is used for communication with the PLC. This field can be left blank in case the H1-TP4 protocol is used and the previous field has to be specified. It is also possible to change the IP address dynamically in case a tag has been specified. When defining a tag then a default value as a IP address must be specified.

This option is not supported under windows NT at the moment.

entry: 

Optional.

entry type: 
ASCII string or TAG .

valid entry:
IP address, 4 digits separated by a dot.



Remote Read Tsap
Remote TSAP identifier for a fetch connection. Must be identical to the local Fetch Tsap of the logical device.

entry: 

Required /default: FETCH.

entry type: 
Alphanumeric string.

valid type: 
String of up to 8 characters.



Read Prio

Priority of the read commands.

Prio 2
Normal data transfer, with maintained connection to a remote node. The  data buffers are dynamically build, during data transfer.

Prio 4
Normal data transfer, with connection establishment and termination. The connection and data buffer are build when data is transferred, and are terminated at the end of the data transfer.

entry:

Required / default: 2.

entry type: 
Decimal number.

valid entry: 
Positive integer 2, 4.



Remote Write Tsap

Remote TSAP identifier for a write connection. Must be identical to the local Receive Tsap of the logical device.

entry: 

Required /default: RECEIVE.

entry type: 
Alphanumeric string.

valid type: 
String of up to 8 characters.

[image: image9.png]Edt View Uilties Est Help

(O[]

Wit | RemoteRov | Rev | Encode | Status Tag Read disable | Write disable
Prio Tsap Pio | DB

z SEND z 10 Status disabieo] disabliel1]
Cancel Enter Next Prev |





Figure 5.3.2 DeltaLink H1 Device definition.


Write Prio

Priority of the write commands. For a description of the priority levels see Fetch Prio.

entry:

Required / default: 2.

entry type: 
Decimal number.

valid entry: 
Positive integer 2, 4.



Remote Rcv Tsap

Remote TSAP identifier for a unsolicited receive connection. Must be identical to the local Send Tsap of the logical device.

entry: 

Required /default: SEND.

entry type: 
Alphanumeric string.

valid type: 
String of up to 8 characters.



Rcv Prio

Priority of the unsolicited receive commands. For a description of the priority levels see Read Prio. The RCV Prio field will not be used in the protocol driver because the PLC Communcations card settings determines what kind of priority this connection will have. This field must be used as an information field for the developer.

The unsolicited receive connection used with PRIO 4 is a special case because in principal Siemens doesn't support a SEND command with PRIO  4 and 'Read/Write yes' configured for the Siemens S5 range (Appendix F). As a consequence DeltaLink has develo​ped a Function Block (FB 2) for S5 to circumvent this problem. This PRIO 4 has been limited for sending Data Blocks only (DBs). When with the SEND command a PRIO 4 connection has been chosen, this FB 2 must be used in the STEP5 program for sending data with the unsolicited receive func​​tion in the protocol driver. For the normal PRIO 2 connection no additional soft​ware is needed in the PLC. For a description of the PRIO 4 FB2 refer to Appendix F.

entry:

Required / default: 2.

entry type: 
Decimal number.

valid entry: 
Positive integer 2, 4.



Encode DB

Data Block (DB) number for encoded write commands. Coded information is placed in this DB, encoding is performed by the PLC. A standard function block (FB10) is pro​vided by DeltaLink for decode actions inside the PLC, for specific infor​ma​tion see also Appendix F and Appendix G.

entry: 

Optional.

entry type: 
Decimal number.

valid entry: 
Positive integer 1 .255.



Status Tag

Real-time database element written to by the Sinec H1 protocol driver task to indicate the status of a communication command. The status element can be referenced by any task to handle communication error situations. A value of zero indicates no error (success), any other values represents an error, for a detailed list of communication errors see Appendix D.

entry: 

Optional.

entry type: 
Standard FactoryLink tag name.

valid entry: 
ANALOG.

[image: image10.png]DeltaLink H1 Device d

Edt View Uilties Est Help

(O[]

Rev | Encode | Status Tag Read disable | Wiite disable | Receive disable
Pio | DB

z 10 Status disabieo] disabliel1]

Cancel Enter Exit Next || Prev





Figure 5.3.3 DeltaLink H1 Device definition.



Read disable
Real-time digital database element used to enable/disable read commands for the lo​gi​cal device.  Read commands are enabled in case there is no tag defined, or the sta​tus of the digital tag is OFF. Read commands are disabled if a tag is defined and the status of the tag is ON.

entry: 

Optional.

entry type: 
Standard FactoryLink tag name.

valid entry: 
DIGITAL.



Write disable
Real-time digital database element used to enable/disable write commands for the lo​gi​cal device.  Write commands are enabled in case there is no tag defined, or the sta​tus of the digital tag is OFF. Write commands are disabled if a tag is defined and the status of the tag is ON.

entry: 

Optional.

entry type: 
Standard FactoryLink tag name.

valid entry: 
DIGITAL.



Receive disable
Real-time digital database element used to enable/disable receive commands for the lo​gi​cal device.  Receive commands are enabled in case there is no tag defined, or the sta​tus of the digital tag is OFF. Receive commands are disabled if a tag is defined and the status of the tag is ON.

entry: 

Optional.

entry type: 
Standard FactoryLink tag name.

valid entry: 
DIGITAL.


Dataset definition

From the display of all the panels, select the DeltaLink H1 Dataset definition panel.

[image: image11.png](O[]
Edi View Uiites Bt Hop
Decoder Data Set Tpe [ 08 [ Sen | tengn ] -
Mailbox Tag
DECODERMBX S | DataSet(0] 0B 50 z 70
DECODERMBX S | DataSet[1] 0B 50 3 2
DECODERMBX S | DataSet[2] 0B 50 10 14
DECODERMBX S | DataSet(3] 0B 50 10 14
DECODERMBX S | DataSet(d] 0B 50 10 14
DECODERMBX S | DataSet[s] 0B 10 0 . [
DECODERMBX S | DataSet[6] 0B 50 30 36
DECODERMBX_S | DataSet(7] 0B 50 30 36
e e m—
Cancel | Enter || B | Next Prev |





Figure 5.4.1 DeltaLink H1 Dataset definition.
The Sinec H1 Dataset Definition panel allows the user to specify datasets for a particular  lo​​gi​cal device. Different logical device names are selected in the panel DeltaLink H1 Device Definition. The name of the logical device is displayed in the field Device Name, at the bottom of the table. Specify the following information.



Decoder Mailbox Tag

Tag name of a decoder mailbox element, to be refe​ren​ced by the Sinec H1 protocol driver task (N.B. IMX must be supported by the decoder task). The decoder task uses this mailbox to receive data from the Sinec H1 protocol driver.

entry: 

Required.

entry type: 
Standard FactoryLink tag name.

valid entry: 
MAILBOX.



Dataset

Tag name representing a (unique) logical name for a dataset. The tag is used inter​nally in the decoder and protocol driver for activating a dataset read from the external device. A dataset is referenced, internally by the decoder and the protocol driver, by the tag name. Therefore the tag specified in this field must be unique. 

entry: 

Required.

entry type: 
Standard FactoryLink tag name.

valid entry: 
DIGITAL.



Type

Type definition of the data area in the logical device (PLC). Note that exception write behaviour depends on the type of data area. To know how an exception write is executed, one should regard the boundary of the data area and the element size involved with the exception write.

entry: 

Required.

entry type: 
Alphanumeric string.

valid entries: 
DB, FB, IB, OB, CW, TW, SW, PB, EB, DX.


description: 


Siemens S5 type


Data type entry
Description

DB
Data Block

FB
Flag byte

IB
Input Byte

OB
Output byte

PB
peripheral byte

CW
counter word

TW
timer word

SW
system data word

DX
expanded data block

DE
Data Block in external memory

EB
expanded peripheral byte

Siemens S7 type


Data type entry
Description

DB
Data Block

FB
Flag byte

IB
Input Byte

OB
Output byte

Siemens TI type


Data type entry
Description

V
Variable

K
Constant

X
Discrete Input (X)

Y
Discrete Output (Y)

C
Control Register (CR)

XP
Discrete Input Packed (X)

YP
Discrete Output Packed (Y)

CP
Control Register Packed (CR)

WX
Word Input (WX or 7MT)

WY
Word Output (WY)

TCP
Timer or Counter Preset (TCP)

TCC
Timer or Counter Current (TCC)

DSP
Drum Step Preset (DSP)

DSC
Drum Step Current (DSC)

DCP
Drum Counter Preset (DCP)

STW
System Status words

DCC
Drum Current count

VF
Variable Memory

KF
Constant Memory

LS
Loop Status

LM
Loop Mode

LKC
Loop Gain

LTI
Loop Reset time (minutes)

LTD
Loop Rate time (minutes)

LHA
Loop High Alarm Limit

LLA
Loop Low Alarm Limit

LPV
Loop Process Variable

LPVH
Loop High Process Variable

LPVL
Loop Low Process Variable

LODA
Loop Orange Deviation

LYDA
Loop Yellow Deviation

LTS
Loop Sample Rate (seconds)

LSP
Loop Set Point

LMN
Loop Output (percent)

LVF
Loop V-flags

LCF
Loop Control Flags

LRSF
Loop Ramp/Soak Status

LERR
Loop Error

LMX
Loop Bias

LHHA
Loop Process Variable High High Alarm

LLLA
Loop Process Variable Low Low Alarm

LRCA
Loop Rate of Change Alarm

LSPH
Loop Setpoint High Limit

LSPL
Loop Setpoint Low Limit

LADB
Loop Alarm Deadband

LHAR
Loop Raw High Alarm Limit

LLAR
Loop Raw Low Alarm Limit

LPVR
Loop Raw Process Variable

LODAR
Loop Raw Orange Dev Alarm Limit

LYDAR
Loop Raw Yellow Dev Alarm Limit

LMNR
Loop Raw output

LSPR
Loop Raw setpoint

LERRR
Loop Raw Error

LHHAR
Loop Raw High/High Alarm Limit

LLLAR
Loop Raw Low/Low Alarm Limit

LADBR
Loop Raw Alarm Deadband

LMXR
Loop Raw Bias

LSPLR
Loop Raw Setpoint Low Limit

LSPHR
Loop Raw Setpoint High Limit

LCFH
Loop Most-sig word loop C-flags

LCFL
Loop Least-sig word loop C-flags 

LKD
Loop Derative Gain Limiting Coef

LRSN
Loop Ramp Soak Step Number

LACK
Loop Alarm Acknowledge Flags

AHA
High Alarm Limit

ALA
Alarm Limit

APV
Process Variable

APVH
Process Variable High Limit

APVL
Process Variable Low Limit

AODA
Orange Deviation Alarm Limit

AYDA
Yellow Deviation Alarm Limit

ATS
Sample Rate in seconds

ASP
Alarm Setpoint

AVF
Alarm Variable Flags

ACF
Alarm Control Flag

AERR
Alarm Error

AHHA
High High Alarm Limit

ALLA
Low Low Alarm Limit

ARCA
Rate of Change Alarm Limit

ASPH
Setpoint High Limit

ASPL
Setpoint Low Limit

AADB
Alarm Deadband

AHAR
Raw High Alarm Limit

ALAR
Raw Low Alarm Limit

APVR
Raw Process Variable

AODAR
Raw Orange Deviation Alarm Limit

AYDAR
Raw Yellow Deviation Alarm Limit

ASPR
Alarm Raw Setpoint

AADBR
Raw Alarm Deadband

AERRR
Alarm Raw Error

AHHAR
Raw High-High Alarm Limit

ALLAR
Raw Low-Low Alarm Limit

ASPLR
Raw Setpoint Low Limit

ASPHR
Raw Setpoint High Limit

ACFH
Most-sig word Alarm C-flags

ACFL
Least-sig word Alarm C-flags

AACK
Alarm Acknowledge Flags

VMM
VME (TI575 only) A24 space

VMS
VME (TI575 only) 16 space

GZ
App Z global variables

GY
App Y global variables

GX
App X global variables

GW
App W global variables

GV
App V global variables

GU
App U global variables

GT
App T global variables

GS
App S global variables

GR
App R global variables

GQ
App Q global variables

GP
App P global variables

GO
App O global variables

GN
App N global variables

GM
App M global variables

GL
App L global variables

GK
App K global variables

GJ
App J global variables

GI
App I global variables

GH
App H global variables

GG
App G global variables

GF
App F global variables

GE
App E global variables

GD
App D global variables

GC
App C global variables

GB
App B global variables

GA
App A global variables

G
Local App global variables



DB

Data block (DB), External Data block (DE) or Data block eXtended (DX) number. Only used if the Type is DB, DE or DX.

In case a TI data type has been specified this number will be used for addressing pages of 64Kb within the data type. Usually this will be set to zero. For example, to address variable with address 65536 in V memory specify DBNR 1 and start address 1.

entry: 

Optional.

entry type: 
Decimal number.

valid entry: 
Positive integer 1 ..255.



Start
Start address number of the dataset. 

entry: 

Required / Default: 0.

entry type: 
Decimal number.

valid entry: 
Positive integer 0 ..2048.



Length

Length of the dataset in bytes or words, depending on the type of the dataset. For the types DB, DE and DX the length is expressed in words, the data boundary is words. For all other types the data boundary is byte, which means that the length is expressed in bytes. Maximum length depends on the type of data set and PLC type, for further details see the Siemens manuals.

entry: 

Required / Default: 1.

entry type: 
Decimal number.

valid entry: 
Positive integer 1 ..2048.

This page is left blank intentionally.


Appendix A. Communication OSI protocol stack installation

A.1 OSI protocol stack for Windows NTI

On the Windows NT platform any Ethernet card with support for Windows NT can be used. This card can be used to run the H1 stack but also in combination with other stacks simultaneously. The stack used for the H1 communication is called the Windows NT TP4 stack. The next section gives a short description of the installation of the stack and how to configure it. This configuration is very important because otherwise H1 communication will not work.

Installation of stack

The TP4 stack delivered with the Sinec H1 driver must be installed through the Control Panel Network applet. The user must have administrator privileges to install the TP4 stack. In this applet the following steps must be taken:

(
From the control panel, select the Network applet and the system presents the network settings dialog box.

· Choose the Protocols tab in the applet and within this tab choose the add button for adding another protocol.

[image: image35.png](O]

Edi View Uiitiss Exst Hel
Device Name Device EthemnetAddress | TCP/IP Address Remote Read Read Remote virte |
Type Tsap Prio Tsap
e EE 080006010001 FETCH 2 RECEIVE
d
Cancel |  Enter | | Exit Next Prev





(
In this applet choose the have disk button and specify the location of the OSI protocol stack. This can be on floppy or on CDROM or hard-disk. In case of the CDROM it is advised to copy first the complete stack to hard-disk and install from there.

· The following pop up window must appear after specifying the right path and pressing the OK button. Press the OK button and the protocol stack will start to install.

[image: image36.png]lect Network Protocol [21x]

Clck the Network Protocol that you want t instal then click OK. If
S youhave an nstalaion sk frtis component cick Have Disk

Network Protoco
ppleT ok P
% DLC Protocol
¥ NetBEUI Protocol
¥ NLink IPX/SPX Compatile Transpart

¥ Paint To Paint Tunneing Prctocel
s e

Have Disk.

Cance





· Before closing the network applet the install procedure will come up with the following window. The local address and the NSAP will be set on default to your computer name and need not to be changed. Pres the OK button to finish the install procedure and reboot the system to activate the protocol stack.

[image: image37.png]Select OEM Option 1

Choose a softwate supported by tis hardware manufaclurer's disk

oK Cancel Help





Configuration

For use with the Sinec H1 driver the stack must be configured. This configuartion will be done automatically when installing the Sinec H1 module through the set_parm utility, which resides in the bin directory of the sinec H1 install directory. This utility configures a few parameters in the registry of NT. The following entries in the registry are altered and can be checked through the regedit utility:

HKEY_LOCAL_MACHINE/System/CurrentControlSet/Services/IsoTp/Parameters

In this directory there are three sub-directories: CLNP, ESIS and TP4. In the directory CLNP the following parameter is changed so it has the following value:

NullNetworkLayer:REG_DWORD=0x1

In the directory TP4 the following parameter is changed so it has the following value:

PropNoChksum:REG_DWORD=0x1

The set_parm utility will stop the protocol stack, make these in the registry and automatically start the protocol stack again. That’s why the preferred order of installing is first the protocol stack, reboot the system and then install the Sinec H1 driver.

Appendix B. Command line parameters

The protocol driver accepts several command line parameters, these can be configured with the configuration manager in the ‘System Configuration’ table, column ‘Program Arguments’. An argument consists out of first a minus sign (‘-‘), followed by the a letter specifying the option. After the letter an optional number can be present, if this is supported by the option.

Option
Description




-dn
Debug option, the level of debug information is set with the number n. The range of this number is from 1 until 9. If no number is specified the default level will be 1. The debug output will be visible in the ‘window’ of the protocol driver, that of the run time manager.




-ln
Same as the previous option, difference is the output device. For this option an ASCII log file is generated, being the file: {FLAPP}/{FLNAME}/{FLDOMAIN}/log/sinec_h1.log




-mn
Defines the size of the pipe buffer for buffering IMX commands from the Ioxlator. The size is specified in kilobytes. The default size 32 Kb which means a value of 32.




-sn
Starts and stops the TP4 stack. The parameter specifies a sleep value in seconds before starting the stack after starting the sinec h1 driver. When stopping the sinec h1 driver the stack will also be stopped.




-c
Automatically disables the connection rebuild after an error on the connection. The disable tag must be forced changed to 0 again for enabling rebuild of the connection. At the first IMX command on the connection, the connection will be tried to rebuild.

This option must be used in case PLC’s are configured but not connected to the network or when frequently connections are lost on the network with a high communication load on that connection.




-LSn
Local Station id with number n, needed if the protocol driver and decoder reside on different nodes (or FactoryLink workstations). This must be an unique (station) number for the network.

Appendix C. Sinec H1 protocol driver error codes

The error code is returned to the user in a user-defined status tag. These error codes will also be printed with the message of the DeltaLink Sinec H1 protocol driver in the run-time mana​ger. The errors can be generated from different parts of the driver which will be listed here:

Error #
XTI layer communication error

4        
Socket marked as non-blocking

9        
Invalid flags for socket

13        
Access error 

14
Socket failure

22
Unable to establish connection, partner not found, invalid TSAP

35
Blocking failed

36
Blocking call in progress

37        
Command already complete

38        
Descriptor is not a socket

39
Destination address required

40       
Data size too large

41       
Protocol is of wrong type for this socket

42       
Protocol option not supported for this socket type

43       
Protocol is not supported

44       
Socket type not supported by this address family

45       
Option not supported

46       
Address family not supported by this protocol

47       
Address family not supported by this protocol

48       
Address is in use

49       
Address not available from local machine

50       
Network subsystem is down

51       
Network cannot be reached

52       
Connection has been dropped

53       
Connection has been aborted

54       
Connection has been reset

55       
No buffer space available

56       
Socket is already connected

57       
Socket is not connected

58       
Socket has been shut down

59       
To many references

60       
Command timed out

61       
Connection refused

91       
Network subsystem not ready

92       
Version not supported

93       
WSAStartup() has not been successfully called

101
Unknown data area

102
Encode value not supported

103
Invalid function code

104
The size off the PG packet was too small

105
Undefined encode destination

106
Undefined exception write

107
No memory available any more

108
Invalid data area

109
Length for read/write is zero

110
Protocol error detected by PLC

Error #
H1 data package errors

201
Unidentified data received.

202
Encode value not supported.

203
Unknown encode type.

204
The size of the H1 packet was too small

205
Error in received H1 protocol header

Error #
H1 data package errors

300
No error.

301
Incorrect Q/Z type at handling block.

302
Area not present in AG.

303
Area in AG too small.

304
AKD Error in the AG.

305
Error with condition code word.

306
No valid ORG format.

307
No free data buffer.

308
No free transport links.

309
Remote error with Read/Write.

310
Data Link error.

311
Handshake error.

312
Initiation error.

313
Abort after reset.

314
Job with boot strap function.

315
Job not present.

316
Area in AG too small.

Error #
FactoryLink errors

401
Internal error

402
Out of memory

403
Operating system error

404
Initialization not successful

405
Initialization not successful

406
Incorrect function

407
Incorrect argument

408
Incorrect data

409
Bad tag

410
Null pointer assignment

411
Change flag not set

412
Procedure table full

413
Bad procedure name

414
Bad user name

415
Bad option

416
Incorrect checksum

417
No options

418
No key

419
Bad key

420
No port available

421
Port busy

422
FL already active

423
No lock

424
Lock failed

425
Lock expired

426
Wait failed

427
Termination flag set

428
Q-size to big

429
Q-size changed

430
No tag list

431
Tag list changed

432
Wake up failed

433
No signals

434
Signaled

435
Not a mailbox

436
No messages

437
Access denied

438
Attribute failure

439
Invalid attribute

440
Attribute not defined

441
Application exists

442
RTDB does not exist

443
No task bit

444
Not a lite task

Error #
IMX errors

450
Bad message type

451
Message with dataset control tag not found in queue

452
No messages available to query

453
Bad receive mailbox tag

454
Bad mailbox send tag

455
Bad dataset control tag

456
Message cannot be adjusted

457
Operation to big for variable

458
Unknown boundary

459
Function not supported

460
No message for this index present

461
The remote dataset Is not defined on this system

462
The received dataset was not registered

463
The message is not queued

464
Message is rejected due error in the remote IMX

465
Illegal method of addressing bits on bit boundary

466
Element cannot be written

467
Invalid buffer specified

468
Block write function impossible

469
Maximum number of messages in MBX reached

470
No memory left

471
Error registering standard dataset

472
Error writing message in pipe

473
Not supported IMX message

474
Error creating pipe

475
Error starting threat

476
Error server connecting to pipe

477
Error child connecting to pipe

478
Error reading the pipe

479
Error number of bytes read from pipe

480
Error writing into the pipe

481
Error number of bytes written into the pipe

482
Error reading dataset from the mailbox

483
No communication buffers assigned

484
Error decrementing semaphore

485
Error writing to pipe, no space left

486
Error querying no. of messages for decoder

487
Max. No. of messages in decoder MBX reached

Error #
Sinec h1 driver status / errors

350
Read functionality has been disabled by the user

351
Write fnctionality has been disabled by the user

353
Invalid addressing method on bit boundary

354
Exception write not possible to destination

355
SINEC_H1 driver has shutdown normally




356
an unknown error occured in the comm layer

357
No data has been received

500
invalid addressing method on bit boundary

501
exception write not possible to destination

502
Sinec H1 driver has shutdown

503
an unknown error occurred in the comm layer

Appendix D. Messages

If an error condition occurs in the protocol driver task during run-time mode, a message to that effect will appear on the runtime manager graphics screen to the right of "SINEC_H1". The error messages that may be displayed are as follows:

Running in DEMO mode

The task did not found the DeltaLink protection code, when starting up. The option file could not be present or damaged. This is a non fatal error, however the task continues running in DEMO mode. The DEMO has a limitation: timed for 5 hours. After shutdown the task can not be restarted without stopping the complete FactoryLink application.
Demo shutdown, licensed to run 5 hours

The task did not found the DeltaLink protection code, when starting up and continued running in DEMO mode. The DEMO has a limitation: timed for 5 hours. After shutdown the task can not be restarted without stopping the complete FactoryLink application.

Demo restart prohibited, restart FactoryLink

The task did not found the DeltaLink protection code, when starting up. The option file could not be present or damaged. This is a non fatal error, however the task continues running in DEMO mode. The DEMO has a limitation: timed for 5 hours. After shutdown the task can not be restarted without stopping the complete FactoryLink application.
Out of RAM

There is not enough RAM memory to load the complete configuration and/or task. This is a fatal error.

Error (%d) reading RTDB element

An error occurred reading a tag value. The error number is displayed.

Error (%d) forcing RTDB element

An error occurred forcing a tag value. The error number is displayed.

Error (%d) writing RTDB element

An error occurred writing a tag value. The error number is displayed.

Error (%d) retrieving event

An error occurred while waiting for an event to happen. The error number is displayed.

Can't open CT file

The task was unable to open the configuration table file, generally because it does not exist. This is a fatal error.

No triggers defined

The task was able to open the configuration table file, but contained not enough information to continue running. This is a fatal error.

Error reading CT index

An error occurred reading the index of the CT file. This is a fatal error.

Error reading CT header

An error occurred reading the header of a table in the CT file. This is a fatal error.

Error reading CT record

An error occurred reading a record of a table in the CT file. This is a fatal error.

Initialization critical parameters failed

Use of critical sections will not be possible, but is still required for full functionality of the pro​to​col driver. This is a fatal error.

Event not registered to FL kernel

Tag event is not registered to the FactoryLink kernel. This is a fatal error.

No decoders defined

There are no decoders (or mailbox) defined. This is a fatal error.

No datasets defined

No dataset is defined, the protocol driver has nothing to do. Therefore this considered to be a fatal error.

Unknown decoder table %s record %d type %d

The protocol driver configuration table file contains an unknown decoder mailbox tag, for the specified table, record number and type of dataset. This is a fatal error.

IMX Bad Mailbox TAG table %s record %d type %d

IMX error, internal error of the protocol driver task. Specified are table number, record number and type number.

IMX (%d) Initialization failed

IMX initialization failed, the error number is reported. This is a fatal error.

IMX (%d) dataset registration failed %s

Registration of the reported dataset failed, the cause can be determined by the error number. This is a fatal error.

IMX semaphore creation failed

Creation of semaphores, needed for IMX failed. This is a fatal error.

IMX failed to start thread

The protocol driver could not start a thread. This is a fatal error.

IMX maximum msg for decoder %d reached

The reported decoder failed to process the queued messages, the configured maximum length of the queue is reached. The protocol driver stops queuing until the number de​creases.

IMX (%d) send error to mailbox %s

The protocol driver could not queue a message for the reported decoder due to an error, the corresponding error number is reported.

IMX (%d) reply to mailbox %s

The protocol driver could not queue a message for the reported decoder due to an error, the corresponding error number is reported.

Com building device failed

Communication error building of a communication device failed. This is a fatal error.

Com unknown DataSet of type %d

Unknown dataset type specified, the type invalid type id is reported. This is a fatal error.
Com init comm. layer %d

An error occurred during initialising the communication layer Specified is the error num​ber.

Com (%d) connecting ‘%s’ %s

An error occurred during connecting to a device. Specified are the device name, func​tio​nality and the error number.

Com (%d) listenening %s %s

An error occurred during listening. Specified is the error number.

Com (%d) accepting connection %s

An error occurred during accepting a connection to a device. Specified are the device name and the error number.

Com (%d) disconnecting ‘%s’ %d

An error occurred during disconnecting from a device. Specified are the device name, functionality and the error number.

Com (%d) read %s

An error occurred during reading from a device. Specified are the device name and the error number.

Com (%d) reading for exception %s

An error occurred during reading from a device for an exception write. Specified are the device name and the error number.

Com (%d) encode write %s

An error occurred during writing for an encoded write to a device. Specified are the device name and the error number.

Com (%d) write %s

An error occurred during writing to a device. Specified are the device name and the error number.

Com (%d) receive %s

An error occurred during receiving from a device. Specified are the device name and the error number.

Com (%d) reject connection %s, %s

An incoming connection request is rejected. Specified is the error number.

Appendix E. Siemens S5-PLC

E.1 Encoded write handling

The Sinec H1 protocol driver is capable to perform an encoded write. An encoded write causes the protocol driver to place coded information in a data block in the PLC instead of di​rect​ly updating or changing a variable. 

The information, placed in the PLC by an encoded write, should be decoded by a PLC-pro​gram in order to update/change the correct variable. A standard function block (FB10) is provi​ded by DeltaLink for decode actions inside the PLC. The standard function block FB10 is cal​led "ENCO-WRT", and uses FB11, FB12 and the data block opened just before calling the function block FB10. The data block opened before calling the function block FB10 must con​tain the information from an encoded write. The protocol driver places the information in a special way in the encode DB. Internally the next flag bytes are used: FB240 .. FB255.


[image: image12.wmf]FB10

NAME: ENCO-WRT


Figure E.1.1 Encoded Write Function Block.
Encode DB



Data word
Type
Description

DW0
KF
Internal use FB10

DW1
KY
Destination, destination type

DW2
KY
DB/DX no., address no.

DW3
KY
Bit no., Change flags

DW4
KF
Value, low word

DW5
KF
Value, high word

DW6
KH
Internal use FB10

DW7
KH
Internal use FB10

DW8
KH
Internal use FB10

DW9
KH
Internal use FB10

DW10
KF
Error code from FB10

DW11
KY
Copy of DW1 for an error 

DW12
KY
Copy of DW2 for an error 

DW13
KY
Copy of DW3 for an error 

DW14
KF
Copy of DW4 for an error 

DW15
KF
Copy of DW5 for an error 

DW16
KH
Internal use FB10

DW17
KH
Internal use FB10

DW18
KH
Internal use FB10

DW19
KH
Internal use FB10

DW20
KH
Internal use FB10

Figure E.1.2 Encode Data Block.

Destination: the information in this byte indicates the destination of the value which should be updated.


Value

Description


M
=
Flag type.


D
=
Data block.


X
=
Data block eXtended.


T
=
Timer.


Z
=
Counter.


A
=
Output.


E
=
Input.


P
=
Peripheral output.


Q
=
Extended periphery output.


S
=
System address.

Destination type: the information in this byte indicates the destination type of the value which should be updated.


Value

Description


F
=
Flag for DB, DX, F, A or E.


B
=
Byte for DB, DX, F, A, E, P or Q.


W
=
Word for DB, DX, F, A, E, P or Q.


L
=
Data left for DB or DX.


R
=
Data right for DB or DX.


D
=
Double word, for long integer or float.

DB/DX number: The information in this byte is the number of a DB or DX. If the destination is not D and not X the value in this byte is irrelevant. The value is between 0 and 255.

Address number: address number of the byte, word, data word, timer or counter.  The value is between 0 and 255.

Bit number: the number of the bit in a word or a flag. If the destination type is not flag, the value is irrelevant.

Change flags: For every encoded write the protocol driver writes the value 255 in this byte. Function block FB10 uses this value to detect if there is new information.

Value: value may be up to words, depending on the type of data. For flag and byte values DR4 is used. For word values DW4 is used. And for long integers and float DW4 plus DW5 is used.

Error code: the different error codes can be:



Error

Description



1

Unknown destination.



2

Unknown destination type for destination is D or  X.



3

Incorrect bit number for destination is D or  X.



4

Unknown destination type for destination is M.



5

Incorrect bit number for destination is M.



6

Unknown destination type for destination is A.



7

Incorrect bit number for destination is A.



8

Unknown destination type for destination is E.



9

Incorrect bit number for destination is E.



10

Unknown destination type for destination is P.



11

Unknown destination type for destination is Q.

E.2 Unsolicited receive PRIO 4

The communication cards CP535 and CP143 are not capable of sending data including read / write information with PRIO 4. The consequences are that the PLC can not send data with PRIO 4 to a FactoryLink workstation to perform an unsolicited receive job. To overcome this problem DeltaLink included a function block (FB2) in the shipment for your H1 driver.

The function block FB2 (UNSOL4) activates a send command on the CP535 or CP143 for PRIO 4. 


[image: image13.wmf]SSNR

A-NR

ANZW

QTYP

DBNR

QANF

QLAE

PAFE

FB2

NAME: UNSOL4


Figure F.1 Unsolicited Receive Function Block.
The function block FB2 uses data block DB11, Flag word MW12. The contents of flag word MW12 and data block DB11 should not be altered by the user. The function block uses also the standard SIEMENS communication functions for SEND and CONTROL (for example: if the PLC type is S-135U, the function blocks will be FB120 and FB123). The parameters for FB2 are identical to the parameters used for the standard SIEMENS communication functions. 

Communication port number SSNR:

A constant of type KY = x, y.

Command number A-NR:

A constant of type KY = x, y.

x = 0 :
Value of x is meaningless and will not be evaluated.

y >< 0 : 
Number of the command for a send-direct. The value zero is not allowed.

Command status ANZW:

Status word for the send command, only a flag word is allowed. The use of a data word will give unpredictable results. For a detailed description of the status word see the SIEMENS manual.


[image: image14.wmf]QTYP

DBNR

QANF

QLAE

DW<QANF>

DW<QANF+1>

DW<QANF+2>

DW<QANF+3>

DB<DBNR>


Figure F.2 Indirect parameters.
Source type QTYP:

A constant of type KC:

Allowed entries 'DB' or 'XX', meaning that the next parameters are direct or indirect.

For indirect parameters QTYP is 'XX', DBNR is the number of the data block where the actual parameters are stored, the start address for the parameters is set with QANF.

Data block number DBNR:

A constant of type KY = x, y.

x = 0 : 
Value of x is meaningless and will not be evaluated.

y >< 0 : 
Number of the data block containing the source data, which will be send.

Source start address QANF:

A constant of type KF, indicating the data word number of the start address for the source data-area. The value of QANF must be greater or equal to 8. The eight data words prior to QANF are used internally by FB2. These data words will be overwritten by the function  block FB2.

Source length QLAE:

A constant of type KF, indicating the length in data words of the source data-area.

Error byte PAFE:

Indication of parameter errors. Valid entries are a flag byte or an output byte. For a detailed description of the error byte see the SIEMENS manual.

E.3 CP143/CP535 Configuration

This section displays the configuration of a CP535 or CP143 card.

   VERBINDUNGSBAUSTEIN

VOM EIGENEN AG:

SSNR          :   0         ANR               :  1

AUFTRAGSART   : FETCH       AKTIV/PASSIV (A/P): P

ZUM FREMDEN AG:

BUKZ:        STKZ:        BGKZ:

ETHERNETADRESSE  : 00AA000682CE H    SSNR:         ANR:

MULTICAST (J/N): N   MULTICASTKREIS:      ETHERNETADRESSE:              H

DATAGRAMM (J/N): N

PRIORITAET     : 2   READ/WRITE (J/N): J

QUELLE/ZIEL    :                LAENGE :

ANZEIGENWORT   :

INTERPRETER    :                ADRESSE:      :      H

EIGENER TSAP-ID: LAENGE: 5    HEXA: 46 45 54 43 48           ASC: FETCH

FREMDER TSAP-ID: LAENGE: 5    HEXA: 46 4C 49 4E 4B           ASC: FLINK

FREMDER NSAP-ID: LAENGE: 12   ASC :

ANZAHL DER AUFTRAEGE PRO TSAP: 1

   VERBINDUNGSBAUSTEIN

VOM EIGENEN AG:

SSNR          :   0         ANR               :  2

AUFTRAGSART   : RECEIVE     AKTIV/PASSIV (A/P): P

ZUM FREMDEN AG:

BUKZ:        STKZ:        BGKZ:

ETHERNETADRESSE  : 00AA000682CE H    SSNR:   0     ANR:

MULTICAST (J/N): N   MULTICASTKREIS:      ETHERNETADRESSE:              H

DATAGRAMM (J/N): N

PRIORITAET     : 2   READ/WRITE (J/N): J

QUELLE/ZIEL    :                LAENGE :

ANZEIGENWORT   :

INTERPRETER    :                ADRESSE:      :      H

EIGENER TSAP-ID: LAENGE: 7    HEXA: 52 45 43 45 49 56 45     ASC: RECEIVE

FREMDER TSAP-ID: LAENGE: 5    HEXA: 46 4C 49 4E 4B           ASC: FLINK

FREMDER NSAP-ID: LAENGE: 12   ASC :

ANZAHL DER AUFTRAEGE PRO TSAP: 1

   VERBINDUNGSBAUSTEIN

VOM EIGENEN AG:

SSNR          :   0         ANR               :  3

AUFTRAGSART   : SEND        AKTIV/PASSIV (A/P): P

ZUM FREMDEN AG:

BUKZ:        STKZ:        BGKZ:

ETHERNETADRESSE  : 00AA000682CE H    SSNR:   0     ANR:  3

MULTICAST (J/N): N   MULTICASTKREIS:      ETHERNETADRESSE:              H

DATAGRAMM (J/N): N

PRIORITAET     : 2   READ/WRITE (J/N): J

QUELLE/ZIEL    :                LAENGE :

ANZEIGENWORT   :

INTERPRETER    :                ADRESSE:      :      H

EIGENER TSAP-ID: LAENGE: 4    HEXA: 53 45 4E 44              ASC: SEND

FREMDER TSAP-ID: LAENGE: 5    HEXA: 46 4C 49 4E 4B           ASC: FLINK

FREMDER NSAP-ID: LAENGE: 12   ASC :

ANZAHL DER AUFTRAEGE PRO TSAP: 1

E.4 PLC Software example

        OB 1  

        NETZWERK 1         0000

        

:A   DB  10 


Call encode datablock

        

:SPA FB   1


Communication link with FL

        
NAME 
:SIE-LINK

        

:O   M    0.0

        

:ON  M    0.0

        

:A   DB  10


Call encode datablock

        

:L   DR   3

        

:L   KF +0

        

:><F



Encoded write performed?

        

:SPA FB 244


Unsollicited receive

        
NAME
:SEND

        
SSNR 
:    
KY 0,0

        
A-NR 
:    
KY 0,3

        
ANZW
:    
MW 110

        
QTYP 
:    
KC RW

        
DBNR 
:    
KY 0,100

        
QANF 
:    
KF +0

        
QLAE 
:    
KF -1

        
PAFE 
:    
MB 114

        

:SPA FB  10


Decode information from FL

        
NAME 
:ENCO-WRT

        

:BE

         DB100               

             0:     
KC 
=
'DB';

Source type

             1:     
KF 
=
+00010;
Source DB number

             2:     
KF 
=
+00001;
Source start address

             3:     
KF 
=
+00005;
Source length

             4:     
KC 
=
'DB'; 

Destination type

             5:     
KF 
=
+00010;
Destination DB number

             6:     
KF 
=
+00001;
Destination start addres

             7:     
KF 
=
+00005;
Destination length

             8:     
KF 
=
+00000;

             9:     
KF 
=
+00000;

            10:    

KF 
=
+00000;

        FB 1  

        NETZWERK 1         0000

        NAME :SIE-LINK

        

:O   M    0.0

        

:ON  M    0.0                    VKE == 1

        

:SPA FB 244                    
Send all

        
NAME 
:SEND

        
SSNR 
:
KY 0,0

        
A-NR
:
KY 0,0

        
ANZW
:    
MW 100

        
QTYP
:    
KC NN

        
DBNR 
:    KY 0,0

        
QANF 
:    KF +0

        
QLAE 
:    KF +0

        
PAFE 
:    MB 104

        

:

        

:O   M    0.0

        

:ON  M    0.0                  
VKE == 1

        

:SPA FB 245                  
Receive all

        
NAME 
:RECEIVE

        
SSNR
:
KY 0,0

        
A-NR 
:    
KY 0,0

        
ANZW
:    
MW 105

        
ZTYP 
:    
KC NN

        
DBNR 
:    
KY 0,0

        
ZANF 
:    
KF +0

        
ZLAE 
:    
KF +0

        
PAFE 
:    
MB 109

        

:***

        NETZWERK 2         001F

        
     
:BE

Appendix F. Siemens S7-PLC

F.1 S7 H1 protocol

The Sinec H1 protocol driver is capable of communicating with a PLC from the Siemens S7 range.  The S7 range of PLC’s supports H1 communication with the following restriction: No read/write header information is incorporated in the transmitted data packages. The consequence are: the read func​tio​na​lity is no longer supported, for write and receive only one dataset (for each functionality) is useful for every device. When defining more then one for e.g. the write functionality means that all data is written to the same location in the PLC. When using this type of communication, the device type specified in the Sinec H1 protocol driver tables must be ‘S7RW’!

A solution for this shortcoming is to use the S7 function blocks (FB5, FB6, FB7) which implements the H1 protocol on the PLC side. To enable the read functionality FB5 should be called once every PLC cycle, the same applies to the write functionality: call FB6 every PLC cycle. The last function block FB7 can be used for the unsolicited receive.

All the functions call internally the following functions:

SFC20, SFC64
These are standard function blocks.

FC5, FC6
These function block are part of the NCM S7 industrial ethernet package and implement the basic receive and send on the PLC side.

The functions blocks (FB5, FB6, FB7) for implementing the H1 protocol on a S7 PLC, use the function blocks FC5, FC6, which are part of the NCM S7 package. These two functions implement the read (FC5) and the write (FC6) service on a connection. There is one important limitation for both function blocks: the maximum length of the data package is 240 bytes! From these 240 bytes are 16 bytes needed to implement the H1 protocol, this result in an effective data length of 224 bytes! 

When defining datasets for the Sinec H1 protocol driver this length of 224 bytes is the maximum length of a dataset, even if the range inside the PLC can be larger.. Trying to write or read a dataset with a length exceeding the 224 bytes will result in an error.

The supported data areas in the S7 PLC, including the maximum addresses and lengths are summarised in the table below.

Supporte Data areas Siemens S7

Data area
Max. 

Db no.
Max. 

address
Description

DB
255
65534
Data block

FB

2047
Flag byte

IB

8191
Input byte

OB

8191
Output byte

FB5: FL_READ

This function block is used to implement the read functionality for the driver, when this function is used the PLC device type definition should be set to ‘S7’ or ‘S5’. The choice between ‘S5’ and ‘S7’ depends on the desired addressing mode of data blocks. When using ‘S5’ data blocks are addressed with words, the ‘normal’ addressing mode for the S5 PLC range. Specifying ‘S7’ means that the driver confirms to the addressing mode on bytes for a data block in a S7 PLC. Note that this information also must be specified as a parameter for the function block.

[image: image15.png]BS

¥BS

S enol
1o oonel oo
169200 {LA0DR ERRORL 0.1
s status| i





Figure G.1.1 Function block FB5.


 Parameters:

Instance DB:
The function block needs an instance DB, specify the desired block number.

ID:
Id of the virtual connection which will be used, id can be found in the connection definition table.

LADDR:
Local address of the virtual connection which will be used, address can be found in the connection definition table.

S5:
Boolean to specify if S5 or S7 addressing mode is to be used. A value of TRUE means that the S5 addressing mode is used. S7 addressing mode is used when the value is FALSE. 

DONE:
Output flag set to TRUE for one cycle on completion of a read job, without an error.

ERROR:
Output flag set to TRUE for one cycle on completion of a read job, with an error.

STATUS:
Output word set to zero on completion of a read job, without an error. If a job ends with an error, the word contains an error code from the one of the following function blocks: SFC20, FC5 or FC6

FB6: FL_WRITE

This function block is used to implement the write functionality for the driver, when this function is used the PLC device type definition should be set to ‘S7’ or ‘S5’. The choice between ‘S5’ and ‘S7’ depends on the desired addressing mode of data blocks. When using ‘S5’ data blocks are addressed with words, the ‘normal’ addressing mode for the S5 PLC range. Specifying ‘S7’ means that the driver confirms to the addressing mode on bytes for a data block in a S7 PLC. Note that this information also must be specified as a parameter for the function block.

[image: image16.png]DEE

E3
S enol——
oonel oo
169200 {LA0DR ERRORL 0.1
s status| i





Figure G.1.2 Function block FB6.


 Parameters:

Instance DB:
The function block needs an instance DB, specify the desired block number.

ID:
Id of the virtual connection which will be used, id can be found in the connection definition table.

LADDR:
Local address of the virtual connection which will be used, address can be found in the connection definition table.

S5:
Boolean to specify if S5 or S7 addressing mode is to be used. A value of TRUE means that the S5 addressing mode is used. S7 addressing mode is used when the value is FALSE. 

DONE:
Output flag set to TRUE for one cycle on completion of a write job, without an error.

ERROR:
Output flag set to TRUE for one cycle on completion of a write job, with an error.

STATUS:
Output word set to zero on completion of a write job, without an error. If a job ends with an error, the word contains an error code from the one of the following function blocks: SFC20, FC5 or FC6

FB7: FL_SEND

This function block is used to implement the unsolicited receive functionality for the driver, when this function is used the PLC device type definition should be set to ‘S7’ or ‘S5’. The choice between ‘S5’ and ‘S7’ depends on the desired addressing mode of data blocks. When using ‘S5’ data blocks are addressed with words, the ‘normal’ addressing mode for the S5 PLC range. Specifying ‘S7’ means that the driver confirms to the addressing mode on bytes for a data block in a S7 PLC. Note that this information also must be specified as a parameter for the function block. Additional parameters include a start condition and a definition of the data area which should be send to the FactoryLink workstation. If the start condition is false, no data transmission will be initiated, but the status of a pending job will be reported on the output parameters.

[image: image17.png]DB7

wa168200

P#DBLO.DBX
2.0 BYTE
20 4

104

en

lacT

Leoor

5

seno

Len

E7

eno

oone|

ErRoR]

sTaTUs

Lro.x

Loz

Lo





Figure G.1.2 Function block FB7.


 Parameters:

Instance DB:
The function block needs an instance DB, specify the desired block number.

ACT:
Activate send command, in case the value is TRUE a send command is started.

ID:
Id of the virtual connection which will be used, id can be found in the connection definition table.

LADDR:
Local address of the virtual connection which will be used, address can be found in the connection definition table.

S5:
Boolean to specify if S5 or S7 addressing mode is to be used. A value of TRUE means that the S5 addressing mode is used. S7 addressing mode is used when the value is FALSE. 

SEND:
Any pointer to identify the area to send to the FactoryLink workstation. Specify the start address and the maximum length of this area. The actual length to send is specified with the next parameter. Note that the maximum length must be greater or equal to the maximum length.

LEN:
Actual length in bytes to send.

DONE:
Output flag set to TRUE for one cycle on completion of a write job, without an error.

ERROR:
Output flag set to TRUE for one cycle on completion of a write job, with an error.

STATUS:
Output word set to zero on completion of a write job, without an error. If a job ends with an error, the word contains an error code from the one of the following function blocks: SFC20, SFC64, FC5 or FC6

F.2 Encoded write handling

The Sinec H1 protocol driver is capable to perform an encoded write. An encoded write causes the protocol driver to place coded information in a data block in the PLC instead of di​rect​ly updating or changing a variable. 

The information, placed in the PLC by an encoded write, should be decoded by a PLC-pro​gram in order to update/change the correct variable. A standard function block (FB10) is provi​ded by DeltaLink for decode actions inside the PLC. The standard function block FB10 is cal​led "ENCODED", and uses SFC20 and an instance data block. The instance data block should contain the information from an encoded write. The protocol driver places the information in a special way in the encode DB.

Encode DB



Data byte
Type
Description

DBB0
KF
Reserved

DBB0
KF
Reserved

DBB2
KY
Destination

DBB3
KY
destination type

DBB4
KY
DB no..

DBB5
KY
address no.

DBB6
KY
Bit no.

DBB7
KY
Change flags

DBB8
KY
Value

DBB9
KY
Value

DBB10
KY
Value

DBB11
KY
Value

Figure F.2.1 Encode Data Block.

Destination: the information in this byte indicates the destination of the value which should be updated.


Value

Description


M
=
Flag type.


D
=
Data block.


A
=
Output.


E
=
Input.

Destination type: the information in this byte indicates the destination type of the value which should be updated.


Value

Description


F
=
Flag for DB, F, A or E.


B
=
Byte for DB, F, A or E.


W
=
Word for DB, F, A or E.


D
=
Double word, for long integer or float.

DB number: The information in this byte is the number of a DB. If the destination is not D the value in this byte is irrelevant. The value is between 0 and 255.

Address number: address number of the byte, word, data word, timer or counter.  The value is between 0 and 255.

Bit number: the number of the bit in a word or a flag. If the destination type is not flag, the value is irrelevant.

Change flags: For every encoded write the protocol driver writes the value 255 in this byte. Function block FB10 uses this value to detect if there is new information.

Value: value may be up to longs, depending on the type of data. For flag and byte values DBB8 is used. For word values DBW8 is used. And for long integers and float DBW8 plus DBW10 is used.

FB10 ENCODED

[image: image18.png]DBLO

B0
en T Enn

ss





 Figure F.2.2 Function Block FB10.

Parameters:

Instance DB:
The function block needs an instance DB, specify the desired block number.

S5:
Boolean to specify if S5 or S7 addressing mode is to be used. A value of TRUE means that the S5 addressing mode is used. S7 addressing mode is used when the value is FALSE. 

F.3 CP443 Configuration

This section displays the configuration of a CP443 card. The following should be defined as a minimum on the S7 (assuming the S7 system configuration is correct):

1.  Remote station, this includes the MAC address of the FactoryLink workstation.

2.  A minimum of three connections must be defined on the CP 443 card. A connection together with one of the function blocks FB5, FB6 or FB7 gives the functionality the driver needs: that is read, write or unsolicited receive!

Remote station definition

[image: image19.png]& s7_h1 - <Offline> (Proiect) (O[]

SIMATIC 57-400 Station 1
MPI Network (1)

SINEC H1 Network (1)

& FactonLink




             [image: image20.png]Propeities - Non-57 Station
StationName: [FactoLink

Station Type
Cs5 C PP @ NonsZ
Node Name Node Type

Propetes.

Delte
Cancel Help





[image: image21.png]Properties - SINEC H1 Nodes

e[ G |
MAC Address: [FoooFe02as48 ¥ Networked
Network
SINECHT

Propetes.

el |t





Connection (TSAP) definition

[image: image22.png]57_h1 \ SIMATIC 57-400 Station 1\ CPU413-1(1)
Connecton Table Edt Inseit PLC View Help

Gl 8l 2| ¢ £ sl ¥

Station: Module:
[SMAATIC 57400 Saton N EE)
Local ID Partner ID
e e Partner Type
R ooy i
0002 AD20 FactoryLink IS0 Transport Connection
0003 AD20 FactoryLink IS0 Transport Connection

Lo o

Displays the propefties o the selected bject for editing. [Row: 1 - Loc. ID: 0001 4020 [Sel 1 of 3





Sinec H1 driver functionality
Function block

Read
FB5

Write
FB6

Unsolicited Receive
FB7

Read connection

[image: image23.png]IS0 Connection

I Opnamics |

e | s
N —
=it

Connestion Endaoint

Local ID (Hex}

o007 AD20 %

Name:

I™ Active Connecton Establishment

Black Parameers

11—

WH1640200 —| LapoR)

el |t




  

[image: image24.png]Propeities - 150 Connection

Ovenviow |

e addosses | oomes |

Descibes the addess paramelers ofthe ocal endpointof an 150
wansport connection.

The TSAPs can be speciiied in ASTIl o 25 a hexadecimal value.

Local Remate.
MAC (HEX]:
TSAP (ASCII) [FNK

TSP (HEX) | [6455¢4348 [45.4C49.4E.48
T54P Lengh: | [5 g

el |t




 

[image: image25.png]BS

¥BS

S enol
1o oonel oo
169200 {LA0DR ERRORL 0.1
s status| i





Write connection

[image: image26.png]IS0 Connection

I Opnamics |

e | s
N —
=it

Connestion Endaoint

Local ID (Hex}

o002A020 %

Name:

I™ Active Connecton Establishment

Black Parameers

2—n

WH1640200 —| LapoR)

el |t





[image: image27.png]Propeities - 150 Connection

Ovenviow |

e addosses | oomes |

Descibes the addess paramelers ofthe ocal endpointof an 150
wansport connection.

The TSAPs can be speciiied in ASTIl o 25 a hexadecimal value.

Local Remate.
MAC (HEX]:
TSAP (ASCII) [FNK

TS8P (HEX): | [5245.4345.4356.45 [45.4C49.4E.48
TS4P Lengh: | [7 g

el |t





[image: image28.png]DEE

E3
S enol——
oonel oo
169200 {LA0DR ERRORL 0.1
s status| i





Unsolicited receive connection

[image: image29.png]IS0 Connection

I Opnamics |

e | s
N —
=it

Connestion Endaoint

Local ID (Hex}

00034020 %

Name:

¥ Active Connecton Establishment

Black Parameers

3—n

WH1640200 —| LapoR)

el |t





[image: image30.png]Propeities - 150 Connection

Ovenviow |

e addosses | oomes |

Descibes the addess paramelers ofthe ocal endpointof an 150
wansport connection.

The TSAPs can be speciiied in ASTIl o 25 a hexadecimal value.

Local Remate.

B | | |
Tsep sy T S—
TSAPHEX) | [3454E44 | |[64casdEME
TPl [T F

el |t





[image: image31.png]DB7

wa168200

P#DBLO.DBX
2.0 BYTE
20 4

104

en

lacT

Leoor

5

seno

Len

E7

eno

oone|

ErRoR]

sTaTUs

Lro.x

Loz

Lo





F.4 PLC Software example

ORGANIZATION_BLOCK OB 1

TITLE =S7 H1 demo

VERSION : 0.1

VAR_TEMP

  OB1_EV_CLASS : BYTE ;           //Bits 0-3 = 1 (Coming event), Bits 4-7 = 1 (Event 

                                  //class 1)

  OB1_SCAN_1 : BYTE ;             //1 (Cold restart scan 1 of OB 1), 3 (Scan 2-n of

                                  // OB 1)

  OB1_PRIORITY : BYTE ;           //1 (Priority of 1 is lowest)

  OB1_OB_NUMBR : BYTE ;           //1 (Organization block 1, OB1)

  OB1_RESERVED_1 : BYTE ;         //Reserved for system

  OB1_RESERVED_2 : BYTE ;         //Reserved for system

  OB1_PREV_CYCLE : INT ;          //Cycle time of previous OB1 scan (milliseconds)

  OB1_MIN_CYCLE : INT ;           //Minimum cycle time of OB1 (milliseconds)

  OB1_MAX_CYCLE : INT ;           //Maximum cycle time of OB1 (milliseconds)

  OB1_DATE_TIME : DATE_AND_TIME ; //Date and time OB1 started

END_VAR

BEGIN

NETWORK

TITLE =Handling of basic communication functions

      CALL FC     1 ;

NETWORK

TITLE =Timer/Counter for H1 demo

      OPN   DB    50; 

      L     T      1; 

      T     DBW    2; 

      T     MW     2; 

      L     C      1; 

      T     DBW    4; 

      T     MW     4; 

      AN    T      1; 

      L     W#16#999; 

      SD    T      1; 

      A     M    100.2; 

      CU    C      1; 

      L     C      1; 

      L     999; 

      >=I   ; 

      R     C      1; 

END_ORGANIZATION_BLOCK

FUNCTION FC 1: VOID

TITLE =S7 H1

//The three functionality’s for H1 communication with FactoryLink are handled

//here:

//1. Read

//2. Write

//3. Unsolicited receive

NAME : H1

VERSION : 0.1

BEGIN

NETWORK

TITLE =FactoryLink Read

//1. FactoryLink read: addressing information is evaluated and the requested data

//   is send to the FactoryLink work station.

      CALL FB     5 , DB     5 (    // FactoryLink read, send requested data

           ID                       := 1,

           LADDR                    := W#16#200,

           S5                       := FALSE,// S7 addressing mode

           DONE                     := M    100.2,

           ERROR                    := M    100.3,

           STATUS                   := MW   110);

NETWORK

TITLE =FactoryLink Write

//2. FactoryLink write: data including addressing info is received, addressing 

//   info is evaluated, and data is set on the correct location.

      CALL FB     6 , DB     6 (    // FactoryLink write, move received data

           ID                       := 2,

           LADDR                    := W#16#200,

           S5                       := FALSE, // S7 addressing mode

           DONE                     := M    100.4,

           ERROR                    := M    100.5,

           STATUS                   := MW   112);

NETWORK

TITLE =FactoryLink unsolicited Receive

//3. FactoryLink unsolicited receive: whenever there is received an encoded write,

//   the addressing information of this write is send back to the FactoryLink

//   workstation.

      L     DB10.DBB    7;          // Check if encoded write is received

      L     0; 

      <>I   ; 

      =     M    100.7;             // Encoded write received, send info back..

      CALL FB     7 , DB     7 (    // Send encoded write info to FactoryLink

           ACT                      := M    100.7,

           ID                       := 3,

           LADDR                    := W#16#200,

           S5                       := FALSE, // S7 addressing mode

           SEND                     := P#DB10.DBX 2.0 BYTE 10,// Origin

           LEN                      := 10, // Length of data in bytes

           DONE                     := M    101.0,

           ERROR                    := M    101.1,

           STATUS                   := MW   114);

      CALL FB    10 , DB    10 (    // Evaluation of encoded write

           S5                       := FALSE); // S7 addressing mode

END_FUNCTION

This page is left blank intentionally.




�{FLINK} is the working directory for the FactoryLink programs.





[image: image34.wmf]
© DeltaLink bv

Printed: 6 aug, 1997
Version 5

© DeltaLink bv
Sinec_H1.doc   Version 5
Page 12
Page 11
Sinec_H1.doc   Version 5
© DeltaLink bv


_930604455.vsd

_930690538

_932386625.doc
��



RAPD







�
















_1000718778.doc


RAPD







�












_930750924

_930690374

_930604307.vsd

_930602771.doc
��



RAPD







�
















